## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR | [49 empty] | 1
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Maharastra Natural Gas Ltd.,Pune
Name of Work: TENDER FOR LAYING & CONSTRUCTION OF 10” NB X 5 KM (Approx.) 600 # UNDERGROUND STEEL PIPELINE NETWORK & ASSOCIATED WORKS FROM GAIL's IP4, SHAHAPURA TO NEAR MEHKAR BYPASS ROAD ON SH 207 & SURROUNDING AREAS IN NANDED GA OF MNGL (SECTION NO. 01)
Tender No: MNGL/CP/2024-25/109
Do you want to quote for this sheet ? |  |  | Yes
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE / SCHEDULE OF RATES (SOR) (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Rate inclusive of all taxes and duties except Goods & Service Tax (Rs.) | Per Unit Goods & Service Tax (GST) In % (To be entered by the Bidder) | GST in Rs. | Unit rate inclusive of all taxes & duties including GST (Rs.) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | CARBON STEEL PIPES | Item1
2 | PIPELINE LAYING / INSTALLATION in all type of surface (Normal/built-up surface) "Receiving and taking over" as defined in the specifications, handing, loading, transportation and unloading of Owner supplied 3-Layer PE coated linepipes from Owner's designated stack-yard to Contractor's stock yard/workshop/work-site including preliminary activities, preparation of drawings, wherever required for crossing etc. including handling, stacking, stringing on the pipeline Right-of-Use/ pipeline route alignment, carrying out inspection of company supplied materials including linepipes at the time of taking over, laying/ installation of coated linepipes, associated burried valves, barred tees, insulating joints, flanges & fittings of all sizes, thickness & ANSI class rating and accessories as per specification wherever required depending on site condition including execution of all works, "taking over", handling , including loading and unloading, transportation of Owner supplied materials other than linepipe from Owner's designated place (s) of issue to work site, | Item2 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3 | additional lands required for Contractor's storage, fabrication, access for construction, procurement and supply of all materials (except Owner supplied materials), consumables, equipment, labour and other inputs, carrying out all temporary, ancillary, auxiliary works, aquistion of ROU/ROW for laying of pipeline from HDD Exit and entry point to Tie in Point of existing Pipeline/ ROU, ready for commissioning of pipeline as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge, including but not limited to carrying out the following works: | Item3 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4 | Surveying of route and detours required at the time of execution including marking the same in topographical sheet, preparation of construction drawings showing survey details, and submit same to Owner for review / approval. | Item4
5 | Staking and installation of construction markers, clearing, fencing, grubbing, cutting of trees, full filling all the requirements of various statutory/ environment authorities to the entire satisfaction of concerned authorities, grading of work area. Shifting of all obstruction within the ROU/ Pipeline route alignment viz. electrical lines/ poles, telephone line / poles, etc. coordination with concerned authorities and obtain permissions from these authorities. | Item5
6 | Trenching to all depths by excavation in all types of soils including soft/ hard rock and different type of pavement / footpath / roads etc. including rock breaking, chiselling or otherwise cutting etc. as required and storing excavated soil, reusable materials at designated area as directed by Engineer in charge and to a width to accommodate the Steel pipeline and MDPE as per the relevant standard/ specification etc. [The minimum depth of the top of pipeline shall be 1.2m measured from top of pipeline coating to the top of undisturbed surface of the soil or as per SCC/ OISD - 141 / 226, whichever is higher]. Dewater of trenches if required as per site condition. | Item6
7 | Carrying out repairs of pipe defects/ replacement in case of irreparable defects and repairs of defects of pipe coating not attributable to Owner including defects/ damages occurring during transportation / handling. | Item7
8 | Stringing of line pipes along pipeline trench / ROU on straw / sand / soft soil bags including supply of bags and its filling materials. | Item8
9 | Checking, cleaning, aligning, bending, cutting and bevelling (as required) of pipes for welding and field adjustments including pipe fittings, welding, carrying out non-destructive testing of welds as required including 100% radiography by X-ray and providing all requisite equipment, labour, supervision, materials, films, consumables, all facilities and personnel to process, develop, examine and interpret radiographs and other tests as required, carrying out repairs of weld joints found defective by Engineer-in-Charge, carrying out re-radiography and other tests as required on repaired joints. | Item9
10 | Carrying out installation of carrier line pipe at all minor crossing viz. carttrack, pathway etc. at designated depth by open cut (except at crossing/Laying along the road by HDD method). | Item10
11 | Carrying out installation of carrier line pipe in the casing pipe at cased crossing (excluding installation of casing pipes which is covered separately). | Item11
12 | Coating of field weld joints, long radius bends (R=3D), elbows, buried fittings and valves etc. including supply of coating materials etc. (i.e. heat shrinkable sleeves and high build epoxy etc.) as per PJS & Technical Specification compatible with 3 layer PE coating material of the line pipe. | Item12 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
13 | Counting the number and type of trees cut in presence of DFO/concerned authorities and keeping record thereof, stacking and handing over of all cut tress. | Item13
14 | Installation / lowering the pipeline in trench to required depth as per PJS, Techanical Specification & drawings, supply & placement of 1.0mm thk. HDPE Yellow colour warning mat,RCC tiles (300 mm width x 50 mm thick) over the pipeline & MDPE Pipe in same trench along the complete route as per standard drawings, data sheets & technical specifications, padding around pipeline as per Standard Drg. no. MNGL/Plng./Steel/03 with suitable soil duly approved by EIC including supply of padding material, backfilling and its compaction to the satisfaction of concerned authorities with excavated earth / borrowed select soil including supply of borrowed select soil duly approved by EIC before backfilling and make ready for restoration to be done by Onwer / concerned authorities. | Item14
15 | Supply and installation of slope breakers, wherever required or, as directed by Onwer / Engineer–in–charge. | Item15
16 | Crossing the all-foreign pipeline / HT line / cable / any other utilities etc. with necessary concrete / HDPE sheet protection including coordination with all agencies and obtaining NOC | Item16
17 | Supply and installation of bank protection alongwith backfill materials duly approved by EIC for pipeline trench and banks falls under minor water body crossing as per technical specification & Std. Drg. No. MNGL/Plng./Steel/28, wherever required or, as directed by Onwer / EIC. | Item17
18 | Training and diversions of streams in steep slope area, wherever required. | Item18
19 | Carrying out air cleaning, pigging, flushing, cleaning and hydrostatic testing of complete pipeline with required quantity of corrosion inhibitor including pre-testing of designated sections complete as per specification and approved by Engineer–in–charge to specified pressures indicated elsewhere and duration after stabilization as per specification, providing all equipment, pumps, fittings, instruments, dead weight tester, pressure recorder, thermocouples etc., and services, supervision, labour, consumables, water including supply of corrosion inhibitor, air, etc. as required, locating of leaks and rectification of defect attributable to Contractor (rectification of defects in linepipe material not attributable to contractor shall be paid separately as per other item of schedule of rate), re-testing after rectification, dewatering after successful completion of hydrotesting of entire section and as per specification | Item19
20 | All tieing-in, including the tie-in(s) of the pipeline with the adjacent sections of pipeline including cutting of test header, rebevelling as required, radiography and other NDT examination, joint coating as per specification. | Item20
21 | Final clean-up of right-of-use or area disturbed by contractor during their construction activities for laying of pipeline works and disposal of debris and surplus material to designated disposal areas and backfilling of trench and compaction of the same as per satisfaction of Owner and / Or as directed by Engineer–in–charge. | Item21
22 | Installation of all burried valves (except extended stem valves) inside the valve pit and making provision to operate the valve. | Item22 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
23 | Preparation of as-built drawings, pipe-books (1 set of tracing on polyester film and 6 sets of as-built drawings and 1 soft copy and 6 hard copies of pipe book) All the works shall be executed in accordance with the provision of contract including carrying out all temporary/ ancillary/ auxiliary works required for the performance of the works and all other acts, deeds, matters and things necessary to make the pipeline ready for precommissioning activities. | Item23 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
24 | Raking up of hard surface of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. Payment for cutting of hard rock, if any, is covered unders SOR no. 77 | Item24 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
25 | Specified dia Thk (mm) Material Coating Type Length of each pipe (mm) NB | Item25 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
26 | 10" NB W.T 6.4mm API 5L X-70, 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item26 | 5000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
27 | Note: This item shall be applicable for the underground steel grid main pipeline & branch pipeline, barred tees, insulating joints, bends, flanges & fittings, accessories etc. (i.e. including arrangement for making provision for tap-off on proposed steel grid main pipeline) and aboveground approach pipeline upto Insulating Joint (excluding installation of aboveground insulating joint) for various stations. | Item27
28 | In above item, restoration works are excluded from contractor's scope, except certain restoration works detailed in clause no. 16C. (V) of 3a. Particular Job Specification under Vol.-I of III. Since restoration works for backfilled pipeline trench shall be done by the concerned authorities / Owner. | Item28 | [53 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
29 | In above item, backfilling of pipeline trench by borrowed soil duly approved by Owner / EIC shall be paid by separate item mentioned elsewhere in the SOR. | Item29 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
30 | Items except above are covered separately. The lengths of pipelines are tentative. | Item30 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
31 | Permission Liasioning /Follow-up | Item31 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
32 | Liasioning & follow up for Permission with all the concerned authorities & boards viz Railways, NH, PWD, MIDC, Local Municipal, Panchyat, Electricity, REC, RES, Sewage water, Drinking water, Forest, Social Forestry, Owners of OFC, Traffic, Law & Order, Fire Brigade, Private Land Owner etc. for entire pipeline length and associated terminals (like SVs, tap-offs) alongwith associated work as per tender. Obtaining necessary NOC from authority after completion of work (Where ever applicable). | Item32 | 5000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
33 | Laying of RCC Tiles | Item33 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
34 | Providing single layer of RCC Tiles with supply of RCC Tiles to entire width of trench above Warning Mat placed in trench over the laid pipeline as per standard drawing, specification and instruction of Owner. (Rate to include cost of all labour, tools, tackles, equipment, hire charges & supply of all materials, etc.) | Item34 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
35 | For width of 10" pipeline trench | Item35 | 5000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
36 | Barricading to comply with HSSE | Item36 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
37 | Steel barricading of the trenches Cautionary Sign Boards and lighting arrangement shall be provided as per attched drawing no.MNGL/Plng./steel/04. The rates include barricading of trenches along with sign boards, lighting etc. and maintain the same till the back filling of the trench. Rates will be payable per metre of BARRICADING PROVIDED. If proper barricading is not provided, MNGL will barricade the trenches at the risks and costs of the CONTRACTOR and will levy penalty of twice the rate per unit for the relevant section of the pipeline apart from other actions as per contract. | Item37 | 5000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
38 | RESTORATION OF ROADS Restoration of asphalt / concrete / red stone roads / pavement/Footpath/Paver block including compaction of soil, to original condition as per requirement and to the entire satisfaction of EIC and / or concerned Owners having jurisdiction for following thickness. | Item38 | [53 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
39 | Restoration of Asphalt road upto 10 cm thickness | Item39 | 400 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
40 | Restoration of Asphalt road beyond 10 cm upto 20 cm thickness | Item40 | 300 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
41 | Restoration of Concrete road upto 10 cm thickness | Item41 | 900 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
42 | Restoration of red stone road / footpath / pavement/ Paverblock upto 4 cm thickness | Item42 | 1100 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
43 | BORROWED SELECT SOIL FOR BACKFILLING Additional work over and above item 1.0 for supply of specified and approved quality of borrowed soft graded soil / sand in place of available excavated material and / or other suitable soil as per applicable standards / specifications, including backfilling of excavated trench for specified length after laying and padding of pipeline, including transportation of such special backfill material over all distances, complete. | Item43 | 800 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
44 | CROSSING OF STEEL PIPELINE BY OPEN CUT | Item44 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
45 | Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insatllation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed. | Item45 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
46 | Road Crossing By Open Cut Method Road Crossings at various locations by Open cut Method along with laying of MDPE upto 180 mm Dia if necessary as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item46 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
47 | Line pipe detail 10" NB, 6.4 mm thk API X-70 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item47 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
48 | Water body Crossing By Open Cut Method kulvert/ canal/ nallah/ drain/ channel Crossings at various locations by Open cut Method along with laying of MDPE upto 180 mm Dia if necessary as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item48
49 | Line pipe detail 10" NB, 6.4 mm thk API X-70 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item49 | 70 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
50 | Note: Laying of the pipeline by the approved method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item50 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
51 | Backfilling of the Road/water/ canal/ nallah/ drain/ channel Crossings/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority. | Item51
52 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item52
53 | CROSSINGS/LAYING ALONG THE ROAD BY HDD METHOD | Item53 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
54 | Complete work of the any crossing (between the limits are defined as approved drawings) by HDD method including "Receiving and taking over" owner supplied three layer PE coated line pipes from Owner's designated place to issue/ dump site(s) and transportation to Contractor's stock yard/ work shop/ work site including all handling loading, unloading, aligning etc. supply of all Contractor supplied material, manpower, equipment, other resources and aquiring the required land for storage, fabrication inclduing string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type Heat Shrink Sleeve and repair of pipeline coating with special repair patch materials as per specification,pre-testing etc. of complete string made for crossing access for Contractor etc and execution of, but not limited to, following works in accordance with specifications scope of work and instructions of Engineer-in-charge and as per all provision of Contract Document. | Item54 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
55 | Pre-construction surveys based on site visit, collection of historical data from irrigation/ concerned department including design & calculation and detail engineering and making of crossing drawing for getting their approval from concerned Authority/ Engineer-in-charge, getting work permit/ NOC for water crossings/ road crossings as well as utility crossings (if any) encountered during crossing prior to start the execution of work. | Item55 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
56 | Directional drilling to required depth from top of road including maintenance of drill hole in all types of strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) at all depth to accommodate the pipeline at all conditions encountered during rail/ road crossing by approved HDD methods for providing minimum cover specified in code/ specification or the actual depth as decided by concerned authority, whichever is more. | Item56 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
57 | In case of water crossing, drilling to the required depth on the banks and bed including maintenance of drill hole in all types of soil strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) all depth to accommodate the pipeline a by HDD methods for providing with minimum cover over top of the pipe at all point across the maximum possible width of water bed (as per drawing) either 1.5 mtrs. below the predicted scour profile expected during the life time of the pipeline or 2.5 mtrs. below the available lowest firm bed (if scour profile/ depth not available) of the water crossing by ascertaining bed level upto 50 mtrs. both the side from crossing location or the actual depth as decided by concerned Authority/ Engineer-in-charge whichever is more. | Item57 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
58 | Laying of the pipeline by the approved HDD method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints with special type Dirax Heat Shrink Sleeve or equivalent and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item58 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
59 | Backfilling of the ditch/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority and all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specification, approved drawings, calculations, methods and to the satisfaction of Engineer-in-charge and/or as directed by concerned Authority. | Item59 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
60 | Post installation hydrotest dewatering and tie-in with pipeline at either side of crossing/banks etc. | Item60 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
61 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item61
62 | Crossing of Road/Drain/channel/Nallah/River crossings by carrier pipeline of size 250 mm NB x 6.4 mm thk. of API X-70 (along with laying of 4'' Steel Pipe for MDPE if necessary) by HDD Method | Item62 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
63 | Laying along the Road by carrier pipeline of size 250 mm NB x 6.4 mm thk. of API X-70 (along with laying of 4'' Steel Pipe for MDPE if necessary) by HDD Method | Item63 | 300 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
64 | Installation of carrier pipes by rock drilling for along the road/Drain/Canal/Channel Crossing/Nallah, or wherever required in all types of hard rock. It includes survey of the underground utilities, submission of profile for approval, execution of the work as per the standard procedure, including , excavation of the pits, insertion/pulling of the carrier pipe, removal of malba, subsequent backfilling and restoration of the facility crossed as per original condition, including supply of all other materials, equipment, consumables, manpower etc including string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type of Heat Shrink Sleeve (Direx) and repair of pipeline coating with special repair patch materials as per Specification, pre-testing etc. of complete string made for crossing/ laying access for Contractor etc. and execution of, but not limited to, following works in accordance with specifications and instruction of Engineer-in-Charge and as per all provision of Contract Document. Balance activities as defined in SOR Item of open trench. Note:The length of HDD mentioned is tentative and may vary to the considerable extent depending upon requirements as per site conditions. The length mentioned in SOR is indicative for all the crossing to be done by HDD, numbers and locations shall be decided by Engineer-in-Charge depending upon site condition. Payment for the length of final tie-in carrier pipeline string with mainline laid by HDD are inclusive in this above item rate. No separate payment shall be made under other clauses mentioned elsewhere. Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item64
65 | Crossing of Road/Drain/Canal/Channel/Nallah/River Crossing crossings by carrier pipeline of size 250 mm NB x 6.4 mm thk. of API X-70 (along with laying of 4'' Steel Pipe for MDPE if necessary) by HDD Method | Item65 | 180 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
66 | Laying along the road by carrier pipeline of size 250 mm NB x 6.4 mm thk. of API X-70 (along with laying of 4'' Steel Pipe for MDPE if necessary) by HDD Method | Item66 | 220 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
67 | Note: (i) Crossing width & Actual string length for HDD shall vary as per design calculations & site condition so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. | Item67
68 | (ii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by HDD method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item68
69 | (iii) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossing at different locations. | Item69
70 | (iv) The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. | Item70
71 | Note: (i) Quantity mentioned under item nos. 53 are indicative only for different location of River/roads/water/ canal/ nallah/ drain/ channel Crossings. (ii) Actual length & width of individual crossing and cover from top of casing pipe/ carrier pipe string may vary depending upon site condition, approved crossing drawings, specifications etc. and / or as decided by Engineer-in-charge/ Concerned Authority. | Item71
72 | (iii) Payment for supply & installation of Zinc ribbon anode and its design excluded from above item and covered elsewhere in the SOR. (iv) Payment for the length carrier pipeline string inserted in casing pipe laid by Boring are covered separately and shall be paid under other clauses mentioned elesewhere in the SOR. | Item72 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
73 | Excavation beyond 1.5m depth in case of crossing of utilities/ drain/ culverts etc. through open cut upto the following depth (including restoration of the damaged area to its original condition and satisfaction of the Engineer-in-charge / concerned authorities) : - | Item73
74 | In all type of surface (Normal/built-up surface) of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. The other activities are as per SOR 1.1. Payment for cutting of hard rock, if any, is covered unders SOR no. 77 | Item74
75 | Deeper than 1.5 m & upto 2.5 m below existing level (for 250 (approx.) mm NB Pipeline) | Item75 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
76 | Deeper than 2.5 m below existing level (for 250 (approx.) mm NB Pipeline) | Item76 | 400 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
77 | Excavation of hard rock | Item77
78 | Excavation of hard rock wherever hard rock of single piece exceeding 1.0 m in length removable by pneumatic chisel/ drill as per direction of EIC. | Item78 | 3600 | Cub. M |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
79 | REPAIR OF COATING DEFECTS (NOT ATTRIBUTED TO CONTRACTOR) | Item79
80 | Repair of Holiday in Coating (Noted and recorded at the time of "receiving and taking over") Supply of all coating repair materials as per requirements of specification to be compatible with line pipe coating material, supply of all consumables, utilities, equipments and all manpower required, pipe cleaning and surface preparation, repairing of coating defects (resulting in holiday) and testing including all handling, transportation, etc. for line pipes, performing all works necessary for the completion of the works stirctly in accordance with relevant specification and instructions of Engineer-In-Charge. This rate shall be applicable per sq. cm of the exposed steel area exposed steel area. | Item80 | 2000 | Sq. cm. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
81 | PERMANENT MARKERS Supply, fabrication and installation of all types of permanent markers along the route including all associated civil works such as excavation in all types of soil, construction in all types of soil, construction of pedestals and grouting with concrete, clearing, supply and application of approved colour and quality of primer and paint, stencil letter cutting for numbers, direction, change etc., restoration of area to original condition and performing all works as per drawing, specification and instruction of engineer-in-charge. | Item81 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
82 | Pipeline RCC boundary / route marker as per drawing | Item82 | 100 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
83 | Pipeline warning markers with post & foundations | Item83 | 34 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
84 | Pipeline direction marker with post & foundations | Item84 | 28 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
85 | Pipeline KM with post & foundations | Item85 | 5 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
86 | HOOK -UP | Item86
87 | Hook-up of proposed pipeline by welding of final tie-in-joint with any existing laid pipeline portion of river X-ing ,existing Tap-off & battery limit of Section I & II including Hook-up point of the existing pipeline to be made ready for welding by cutting of flanges / valves / headers at all depth in all type of soil etc. Venting of N2 / gas / gas mixture as required purging of N2 Gas (if required), rebevelling as required, radiography and other NDT examination, joint coating as per specification.Contractor shall supply of all consumables, manpower, machinaries, materials, N2 gas etc. and carry out all works as per the provisions of Contract document and instructions of Engineer-in-charge. | Item87 | [53 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
88 | For 10" NB 600 # | Item88 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
89 | PRE-COMMISSIONING AND ASSISTANCE IN COMMISSIONING OF PIPELINE SYSTEM Swabbing, drying, purging with nitrogen of the complete pipeline network and the associated facilities being installed to the specified acceptance criteria, carrying out pre-commissioning works, providing assistance during the complete duration of commissioning operations for entire pipeline network system including supply of all equipment, man-power, consumables (including pigs & nitrogen required for purging with maintaining nitrogen column of mininum 10% of pipeline geometric volume) materials for all temporary works and performing all associated works, complete as per the relevant specifications, other provisions of Contract document and instructions of Engineer-in-charge. | Item89 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
90 | For 10" NB 600 # | Item90 | 5000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
91 | IDLE TIME PRESERVATION OF PIPELINE Preservation of complete pipeline and associated facilities forming part of the pipeline as per Bid document and its maintenance including supply of all consumables, all equipment, manpower, etc. complete as per the requirements of specifications, other provisions of Contract document and instructions of Engineer-in-charge. Note : Owner reserves the right to exercise either or none of the rates below. | Item91 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
92 | By filling and pressurizing with nitrogen to a pressure of 2 bar(g) for a period of 3 months. | Item92 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
93 | For 10" NB 600 # | Item93 | 5000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
94 | For every additional period of one month or part thereof | Item94 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
95 | For 10" NB 600 # | Item95 | 5000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
96 | RCC VALVE PITS All civil works including supply of all materials, excavation of pit, piping supports including all PCC and RCC works for valves pits including pedestals with insert plates as required sealing of pipe at valve pits, providing cover etc. and finishing , clean-up and restoration of site, filling and grading of area around valve station for avoiding any local flooding of area, as per typical drawing and specification enclosed and instructions of Engineer-in-charge. In this item, instead of Brick Work, RCC will be done | Item96 | [53 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
97 | Valve Pit of Size 2m x 2m | Item97 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
98 | Valve Pit of Size 1 m x 1 m | Item98 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
99 | SUPPLY OF ASSORTED PIPE, FITTINGS AND FLANGES Complete works of supply of pipes, flanges & fittings for aboveground & underground installation including all taxes, duties, transportation and inspection charges but not limited to, the following items in accordance with PMS (piping material specification), relevant specifications & drawings indicated in job specification under SCC (technical) and instructions of Engineer-in-charge and as per all provisions of the CONTRACT DOCUMENT. - Handling including lifting, transportation from Contractor Stores to CONTRACTOR's workshop for fabrication and/ or to work site for field fabrication and erection for all piping items supplied by Contractor. | Item99 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
100 | Carbon Steel Pipe (A 106, Seamless B-36.10/ API X 70 ) | Item100 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
101 | Size Rating/ Schedule | Item101 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
102 | 2" NB, BE Sch. 80 | Item102 | 40 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
103 | 1" NB, PE Sch. 80 | Item103 | 38 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
104 | ¾" NB, PE Sch. 160 | Item104 | 36 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
105 | Flanges | Item105 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
106 | Weld Neck (B-16.5, 600# A105,125 AARH, Serrated finish) | Item106 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
107 | Size Rating/ Schedule | Item107
108 | 2" NB, RF End thickness to match with pipe wall thickness (SCH 80) | Item108 | 15 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
109 | Blind Flanges (B-16.5, 600# A105,125 AARH Serrated) | Item109 | [53 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
110 | Size | Item110 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
111 | 2" NB, RF | Item111 | 15 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
112 | Elbow (Seamless) | Item112
113 | 90° Elbow (MOC MSS SP 75 WPHY 70 R= 3D ) Min Thickness 6.4mm | Item113 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
114 | Size Rating/ Schedule | Item114 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
115 | 10" NB 600# | Item115 | 25 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
116 | 45° Elbow (MOC MSS SP 75 WPHY 70 R= 3D ) Min Thickness 6.4mm | Item116 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
117 | Size Rating/ Schedule | Item117 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
118 | 10" NB 600# | Item118 | 25 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
119 | 22½° Elbow (MOC MSS SP 75 WPHY 70 R= 3D ) Min Thickness 6.4mm | Item119
120 | Size Rating/ Schedule | Item120
121 | 10" NB 600# | Item121 | 22 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
122 | 11½° Elbow (MOC MSS SP 75 WPHY 70 R= 3D ) Min Thickness 6.4mm | Item122 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
123 | Size Rating/ Schedule | Item123 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
124 | 10" NB 600# | Item124 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
125 | Tees (Seamless) | Item125
126 | Equal Tee (MOC MSS SP 75 WPHY 70 & DIM. ASME B16.9) | Item126
127 | Size Rating/ Schedule | Item127
128 | 10" NB x 10" NB x 10" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item128 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
129 | 2" NB x 2" NB x 2" NB Sch. XS | Item129 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
130 | Reducer (MOC MSS SP 75 WPHY 70 & DIM. ASME B16.9) | Item130
131 | 10" NB x 6" NB Min Thickness 6.4mm | Item131 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
132 | 10" NB x 4" NB Min Thickness 6.4mm | Item132 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
133 | 12" NB X 10" NB Min Thickness 6.4mm | Item133 | 2 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
134 | 4" NB X 2" NB Min Thickness 6.4mm | Item134 | 2 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
135 | 10" NB X 8" NB Min Thickness 6.4mm | Item135 | 2 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
136 | Weldolet and Sockolet | Item136
137 | Weldolet (MOC A105 & DIM. MSS SP 97) | Item137
138 | Size Rating/ Schedule | Item138
139 | 10" NB x 2" NB Sch. 80. (600#) | Item139 | 10 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
140 | Sockolet (MOC A105 & DIM. MSS SP 97) | Item140
141 | 10" NB x 3/4" NB 600 # | Item141 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
142 | Butt Weld Disc End Cap (MOC MSS SP 75 WPHY 70 & DIM. ASME B16.9) | Item142 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
143 | Size Rating/ Schedule | Item143 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
144 | 10" 600 # | Item144 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
145 | Fabrication & Installation of Underground Valve Assembly (including Pneumatic testing of Assembly before installation at Design Pressure) | Item145 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
146 | 10"NB Isolation Valve/tap-off assembly as per Drg. No. MNGL/Plng./Steel/40 | Item146 | 5 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
147 | Note: | Item147
148 | For all the supply items mentioned above, procurement shall be made as per enclosed Data Sheets and respective technical specification, after due approval of Engineer-in-charge. | Item148 | [53 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
149 | The quantities mentioned above are tentative and quantities for above supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item149 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
150 | OFC | Item150 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
151 | Supply of 24 Fibre Composite armored Optical Fibre Cable drum (24 Fibres as per ITU-T G652D) of 5 km +/-5% Cable drum length with, Two number electronic locater as per PTS-Optical Fibre cable. | Item151 | 5000 | m |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
152 | Supply of 40 MM Permanently Lubricated HDPE duct along with all the required accessories | Item152 | 5000 | m |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
153 | Laying of HDPE duct with Steel Pipeline | Item153 | 5000 | m |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
154 | Blowing of Optical Fibre Cable inside HDPE Duct/conduit | Item154 | 5000 | m |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
155 | Supply and Installation of Inspection chamber | Item155 | 5 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
156 | Supply & Installation of Electronic marker | Item156 | 5 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
157 | Splicing, Jointing of optical fiber cable , final Jointing / splicing, Testing of OFC after jointing all completed as per specifications | Item157 | 5 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
158 | PLANT PIPING (ABOVEGROUND) Fabrication and testing of carbon steel piping and fittings, valves, IJ, including supply of all consumables, equipment, manpower, and other resources and execution of job as per instruction AIC/EIC.Transportation of all piping items from Owner's and/ or Contractor's storage point to work at site/ workshop as applicable, complete work of fabrication, erection, painting, testing of pipes, flanges and fittings and making ready for further Commissioning / Start-up of carbon steel piping of all sizes and ratings including supply of all consumables, equipment, manpower and other resources and execution of, but not limited to, the following works in accordance with relevant specifications indicated in item 5.5 of PJS & scope of work indicated in SCC, drawings, specification and instructions of Engineer-in-charge and as per all provisions of the CONTRACT DOCUMENT. | Item158 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
159 | Fabrication including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site, cutting, edge preparation, inclusive of grinding the edges of pipes, fittings, flanges, reducers etc. to match with the matching edges of uneven thickness, wherever required, fit-up, welding of pipes and fittings like elbows, tees, reducers, weldolets, sockolets, Valves, IJ etc. flanges, vent and drain point connection, Radiography and NDT of all joints etc, including providing stubin connections, fabricated fittings and reinforcement pads etc., as required. | Item159 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
160 | Erection of pipes of all types and thickness at all elevations, connecting with equipment nozzle, aligning, installation and carrying out connected activities for all types of valves, all online instruments and fittings of all sizes of elbow, reducers, tees, flanges, blind flanges, spectacle blind flanges, branch connection / tapping for pressure gauges, including installation of gaskets and bolts. | Item160 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
161 | Erection including prior cleaning, lifting, placing on pipe sleepers and supports, overhead on racks, skids and at all elevations including installation and carrying out connected activities for all types of valves including supply and fixing of gaskets, studs/ bolts, nuts wherever required for all sizes, levelling, aligning, joining of flanges, blind flanges, connecting with equipment, nozzles, strainers, tie-in with existing piping/facilities, etc. tapping for inline instruments like pressure gauges, thermowells, sample connection, etc. | Item161 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
162 | Hydro testing of the piping job shall be conducted at pressure mentioned in specification for a period of 4 hours by using de-mineralised water, to check its strength. No visible leakages shall be detected during the test. Testing shall be conducted as per tender specification.Pneumatic Testing of entire above ground piping at Design pressure before final hook up. | Item162 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
163 | Preparation of final bill of material based on piping GADs. | Item163 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
164 | Preparation of isometric and fabrication drawings. | Item164 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
165 | Carrying out Non-destructive testing as required except items mentioned in sl. no. 228 of SOR. | Item165 | [53 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
166 | Painting of entire system (including aboveground all pipes fittings, flanges and accessories) as per specifications suitable for highly corrosive area environment including supply of approved paints and primers, application of primer and paints, indentification lettering/ numbering, colour coding, etc. as specified including rub down & touch up of shop primer or scrapping of shop primer wherever required by COMPANY and providing scaffolding for all heights etc. | Item166 | [53 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
167 | Cleaning and flushing by water/ compressed air, testing of the systems including hydrostatic, pneumatic and any other type of testing as specified, draining, drying by compressed air/other methods approved by COMPANY. | Item167 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
168 | Precommissioning & making operational all piping system and equipments. | Item168 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
169 | Commissioning Contractor scope shall provide all necessary assistance in term of supply of man-power, equipment, tools and tackles required amount of nitrogen for purging of entire terminal piping system including equipments etc. to the company during commissioning activities. | Item169 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
170 | Completion of all such work in all respects as per scope of work and as per drawings, specifications and instructions of the COMPANY and keeping the system ready in all respects for further commissioning and start up. | Item170 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
171 | Hook-up works (with client/ consumer piping at battery limits): | Item171 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
172 | Complete Carbon Steel aboveground Piping Work with painting including all fittings, flanges and supply of all required gaskets, studs bolts & nuts etc. and Any other work and material required for the completion of the work and not covered above and desired by EIC shall be in the scope of contractor | Item172 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
173 | Carbon Steel Pipe (ASTM A 106, Seamless B-36.10 / API X 70) | Item173 | 500 | inch Dia |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
174 | 1) Pipe Specification and thickness may vary depending upon availability of pipe. No extra payment shall be made for this. 2) All butt welded fittings & flanges end shall generally match with connecting pipe wall thickness. However, in case of misalignment, Contractor shall have to do end preparation without any extra cost. 3) All o-lets less than 2" NB size, all sizes of coupling and nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under erection rate. | Item174 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
175 | Aboveground installation of Insulating Joint & Valves etc. Handling including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site and installation of all types of valves, insulating joint including assembly of valve accessories, (if any) by bolting, threading or welding, supply and insertion of gaskets, nuts & bolts, nipples, etc. at all elevations of pipe sleepers, supports or overhead on racks, equipments nozzle, skid & painting etc. supply of all consumables, manpower, equipment, etc. for completion of all works as per scope of work and as per drawings, specifications and instructions of Engineer-in-charge including servicing/ cleaning of valve wherever requried. | Item175
176 | Welded Valves (Full Bore/ Reduced Bore) Ball / Globe / Check Valve | Item176
177 | Size Rating/ Schedule | Item177
178 | 10" NB 600# | Item178 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
179 | 2" NB 600# | Item179 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
180 | Sockolet Welded Valve (Ball / Globe Valve) | Item180
181 | Size Rating/ Schedule | Item181
182 | 1" NB 800# | Item182 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
183 | ¾" NB 800# | Item183 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
184 | Insulating Joints | Item184 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
185 | 10" NB, 600# - Insulating Joints | Item185 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
186 | STRUCTURAL WORKS | Item186 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
187 | Supply of erection of single leaf mild steel gate 2.5m high with mesh upto 2m height and barbed wire fencing and 2m wide complete in all respect including painting as per TS on all MS items, all works as per specification and drawings excluding foundations and RCC beams. | Item187 | 10 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
188 | Supply of all materials, fabrication and erection of chain link fencing 2.5m high with mesh up to 2m height and barbed wire fenching complete in all respects including painting as per TS on all MS items, all works as per specification and drawings excluding foundation and RCC beams. | Item188 | 180 | RM |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
189 | Pipe Supports & Other Structures | Item189 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
190 | Supply, fabrication and erection of all types of pipe supports like clamps, saddle, guide stops, cradles, turn buckles, anchors, T-posts; stockade/ trestle and pipe bridge for overhead piping; frames for canopy, approach ladders and platforms, crossover, cable tray supports, etc. including painting suitable for highly corrosive area as per specification labour and supervision & complete work as per drawings, specifications and instruction of Engineer-incharge. (Bolts, nuts, washers, U-clamps etc. for supporting shall be supplied by the Contractor within the rates quoted. These items will not be measured and paid seperately). The work is to be completed in all respect as per scope of work and specification. | Item190 | 300 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
191 | Notes: | Item191 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
192 | The quantities indicated are estimated values and hence are approximate. Final payment will be made based on actual quantities to be certified by the Purchaser. | Item192 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
193 | The cost of MS bolts (permanent and service(, washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants etc., as required for the work shall be deemed to be included in the quoted rates. | Item193 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
194 | All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accrodance with time schedule, are deemed be included in the quoted rates. | Item194 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
195 | CIVIL WORKS | Item195 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
196 | Site Grading Excavation in earth and filling to the grades and levels shown in the approved drawings in all kinds of conditions including for Road embarkments, using approved quality good earth from designated borrow area, for all heights and depths including clearing and stripping (min. 150mm) of the area marked for filling, taking spot levels, consolidating the exposed natural soil surface, excavating the earth from borrow area loading, transporting & unloading, spreading in layers not exceeding 150mm thickness, breaking clods, watering (if reqd.), ramming and compacting by manual/ mechanical means to give minimum 92% of modified Proctor's density of earth, testing & dressing including disposal of all unserviceable material all complete as per specifications and directions of Engineer-in-charge. | Item196 | 200 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
197 | (Rate to include cost of all labour, tools, tackles, equipment, hire charges, cost of borrow earth by way of royalties, right of way, cess etc., as applicable with all bye works and sundry works). | Item197
198 | Plain Cement Concrete Supplying and laying plain cement concrete (including shuttering of required) in all types of concrete works including levelling courses below foundation, substructure, superstrcuture, chambers, cable tranch, under floors and any other locations, at all leveies as per drawings, specifications and directions of the Engineer-in-charge. | Item198
199 | PCC 1:2:4 1 Cement : 2 Coarse sand : 4 stone aggregate 20mm nominal size. | Item199 | 300 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | #VALUE!
200 | Reinforced Cement Concrete Providing and laying reinforced cement of grade M-20 with 20mm and down grade crushed stone aggregate in all types of structures like foundations, pedestals, pedestal bases, pipe supports, sleepers cable trench inlcuding constrcution joints, bitumen painting on surface in contact with soil, providing and fixing reinforcing steel, shuttering, inserts, finishes etc. at all depths and heights complete as per drawings, specifications and direction of the Engineer-incharge. | Item200 | 500 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | #VALUE!
201 | Rate to include cost of all labour, tools, tackles, equipment, hire charges, supply of all maerials such as minimum 43 grade cement including sulphate resistant cement for substructures, R/F steel, Inserts, bolts, conduits, bitumen, other minor constrcution materials, shuttering, stanging, earthwork in excavation and backfilling using serviceable earth in all conditions, shorting bailing and pumping out water, testing of concrete, curing etc. with all bye works and syndry works. | Item201
202 | TEMPORARY CATHODIC PROTECTION SYSTEM | Item202
203 | Design, detailed engineering, supply, installation, testing and commissioning of the temporary Cathodic protection system using Mg/ Zn galvanic anodes to protect the external surface of 3 LPE coated entire 5.5 (approx.) long steel pipeline network against corrosion for design life of minimum 1 year or till commissioning of PCP system whichever is later as per standard specification No. MNGL/Steel/TS/15 for temporary cathodic protection system. Scope shall also include but not limited to the following for completion of jobs: | Item203
204 | Measurement of soil resistivity along the right of way of the main pipeline route as per specification for design & installation of anodes. | Item204
205 | Collection of additional data related to cathodic protection along the right of way of pipeline as per specifications. | Item205 | [53 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
206 | Supply, installation, testing & commissioning of one set of spark gap arrestor with 2 plate Zinc grounding cell of 20 kg net weight each across each insulating joint as per specification. | Item206 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
207 | Supply, installation, testing & commissioning one set of polarisation cell with zinc anode at all high tension (66KV or higher) electrical power transmission line/Equipment crossing or running parallel to the pipeline for grounding purpose as per specification. The rating shall depend upon anticipated fault current & ground bed resistance at the location of installation. However, the rating of polarisation cell (krick) shall not be less than 5 KA & number of 20 kg net weight zinc anode shall not be less than two. | Item207 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
208 | Supply & installation of Zinc Ribbon Anodes at 4-8 O’Clock position in the interval of 2 metre (max.) on carrier pipes at all cased crossings i.e. railways/ roads etc. | Item208 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
209 | Monitoring of the protection system for 6 months. | Item209 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
210 | All civil/ structural works related to TCP system including supply of bricks, cement & steel etc. required for completion of the system. | Item210 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
211 | For 10" | Item211 | 5000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
212 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item212 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
213 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item213 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
214 | FIELD INSTRUMENTATION | Item214
215 | PRESSURE INSTRUMENTS | Item215 | [53 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
216 | Supply , Installation of Pressure Gagues and their accessories inclusive of supply of necessary piping materials and tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/ manifolds & hydraulic testing (exclusive of calibration of instruments) as per installation standard attached elsewhere in Tender Document and Supply as per Data Sheet No.MEC/23K8/05/E5/I/001/DS-PG. Give breakup of supply and Installation rate. | Item216 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
217 | CALIBRATION | Item217
218 | Calibration of the instruments listed below including removal of instruments from pre-installed locations like panels, enclosure racks, fields etc. and refixing them back in respective/ required places, providing equipments, necessary test jigs, instrument air and all consumables. Calibration reports shall be prepared and to be submitted to the Purchaser/ Consultant. | Item218 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
219 | Pressure Gauges | Item219 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
220 | Note: | Item220 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
221 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item221 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
222 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item222 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
223 | PIPING WORKS FOR SECTIONALISING VALVE STATION-CUM-TAP-OFF POINT All works for fabriaction and installation of all piping above ground at all elevations and below ground at all depth for Sectionalising Valve Station alongwith preparation of construction drawings duly approved by EIC, in all type of terrains and soils including transportation and handling of all Owner supplied materials i.e. extended stem butt welded sectionalising gas actuated ball valve, other types of valves, line pipes for mainline, 4" NB pipe for all branch line including ventlines from Owner's designated place(s) of issue to work site. | Item223 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
224 | Contractor shall supply all required size & type of piping material like pipes, fittings & flanges etc. as per PMS alongwith 2" NB pipe for all branch line & vent line (wherever required) including supply of all consumables, manpower, machinaries, materials etc. and carrying out all mechanical works of underground and above ground piping including fabrication, welding, nondestructive testing of welds, weld repairs/ retesting, cleaning/ flushing, pre-hydrotesting & hydrostatic testing, dewatering, functional testing, cutting of mainline and bevelling (if required) | Item224 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
225 | assembly, including radiography of tie-in joints, corrosion, coating and external painting as required, installation of instruments like pressure/ temperature instruments/ gauges alongwith complete SS Tubing works including supply of SS Tube and thier accessories etc., as required, obtaining all statutory clearances, approvals and permissions for the works (wherever required), making of valve pit (for detail refer relevant drawings) for SV Stationscum- tap-off points enclosed with tender filled with sand, excavation and filling in all types of soils including soft/ hard rock for installation of piping/ pipe supports providing pipe supports, area fencing and gate including all associated civil and structural works; painting, finishing, clean-up and restoration of site; preparation of as-built drawings, documents and project records and performing all works as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge. In this item, instead of Brick Work RCC will be done | Item225 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
226 | Type - I SV Station on 10" Pipeline | Item226 | 1 | Lumpsum for each |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
227 | Note: i) Work under above items are exclusive of all works associated with main pipeline covered under Item No. 1.0 above. ii) All civil/ structural works including area fencing and gate, valve pits except for piping support will be paid separately as per unit rate provided elsewhere in the SOR. iii) All coupling, nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under above item rate. | Item227 | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
228 | Laying of MDPE pipe along with Steel pipe line Excluding supply of all MDPE pipe (PE 80/100,SDR11), but Including supply of Bends, Couplers, End caps, Tees, PE Reducer, CS to PE Fitting, Saddle Tapping, Warming mat, etc. as required to complete the job. ( Particular job specification.) "Receiving and taking-over" as defined in the specification, handling, loading, transportation and unloading of Owner supplied MDPE line pipes (PE80/100, SDR11) of all sizes (as free issue items) from Owner's designated place(s) of issue to Contractor's own stock-yard(s)/ Work Shop(s)/ work-site(s) including proper storing, stacking, identification, providing security & insurance cover , including supply of accessories of all sizes & thickness like Bends, Couplers, End caps, Tee, PE Reducer, CS to PE Fittings, Saddle Tapping, Warning Mat, etc.. | Item228
229 | Stringing/ uncoiling of the MDPE line pipe on the pipeline Right-of-Use, laying/ installation of MDPE line pipe alongwith steel pipeline (alongwith installation of required accessories as mentioned above) of following sizes, including executing all works; fabrication, access for construction; supply of all materials (except Owner supplied materials), consumables, labour and other incidental works and handing over the same after return of the surplus pipes to the Owner's designated stockyard(s); carrying out all temporary, ancillary, auxiliary works required to make the MDPE pipeline ready for commissioning as per drawings, specifications, scope of work indicated in PJS and other provisions of Contract document and instructions of Engineer-in-charge. | Item229
230 | UP to Dia 90mm | Item230 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
231 | Dia 125mm | Item231 | 5000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
232 | Note : The quantities indicated above against all individual item are tentative and may vary considerably depending upon site condition, methodology adopted as per site requirement with due approval of Owner/ Consultants. | Item232
233 | Details of Major Road Crossing (NH/SH/MDR/MSRDC): Supply, Installation & Insertion of pipeline across Canal / State Highways as per SCC and technical specifications | Item233
234 | Supply & Installation of 24" NB x 6.4mm Wall thk. Casing pipe for Line Pipe 10"NB(6.4 mm thk API 5L Gr X70) & 4" NB, 6.4 mm thk API 5L Gr. X70 pipe by Jacking Boring . Including Insertion of 10" dia and 4" dia (for 125 mm dia MDPE Connectivity) Carrier pipeline in 24" dia casing pipe and connectivity with existing pipeline at both end of National Highways/State Highways/ Railway as per SCC and technical specifications -Supply of Casing Pipe Supply of following casing pipe including handling, loading, transportation & unloading etc. to contractor's own stock yard / worksite(s). -After Completion of insertion of carrier pipe with Connectivity at both end including all works as per the scope of work -Post Hydro testing & Commissioning , Submission of as-built drawing, Submission of Documents - The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. - Rate Should include supply & installation of 250mm Casing pipe for 4" Steel Pipeline for MDPE (if required by Authority & as per the instructions of EIC) | Item234
235 | Note: (i) Crossing width may vary as per site condition. Tenderer are advised to visit site for actual assessment of extent of crossing. Actual length of Boring shall be as per design calculations so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. (ii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by Boring method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item235
236 | (iii) The Contractor has to quote alongwith 4" NB (for 125mm MDPE). No any extra payment shall be made against this item. (iv) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossings at different locations. | Item236
237 | (v) Actual length & cover from top of casing pipe string may vary depending upon site conditions, approved drawings, specification etc. and / or as decided by concerned Authority / Engineer-in-charge. (vi) No Extra Payment for supply & installation of Zinc ribbon to be provided to Carrier pipe & Zinc Anode is to be provided to Casing pipe and its design included in above item | Item237
238 | Supply and installation of 24'' casing pipe,Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insertion of carrier pipe in casing pipe after above ground pretesting at specified test pressure and installation of casing insulators & Zinc ribbon anode as per specification/ drawings. Installation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed (Any type of soil) | Item238 | 80 | Mtrs |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! |  | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
Total in Figures | [51 empty] | 0 | 0 | #VALUE! |  | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## BoQ2 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR | [49 empty] | 1
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Maharastra Natural Gas Ltd.,Pune
Name of Work: TENDER FOR LAYING & CONSTRUCTION OF 10” NB X 5 KM (Approx.) 600 # UNDERGROUND STEEL PIPELINE NETWORK & ASSOCIATED WORKS FROM NEAR MEHKAR BYPASS ROAD ON SH 207 TO MNGL'S CGS NEAR VEDIKA LAWNS, MEHKAR & SURROUNDING AREAS IN NANDED GA OF MNGL.(Section No-02)
Tender No: MNGL/CP/2024-25/109
Do you want to quote for this sheet ? |  |  | Yes
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE / SCHEDULE OF RATES (SOR) (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Rate inclusive of all taxes and duties except Goods & Service Tax (Rs.) | Per Unit Goods & Service Tax (GST) In % (To be entered by the Bidder) | GST in Rs. | Unit rate inclusive of all taxes & duties including GST (Rs.) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | CARBON STEEL PIPES | Item1
2 | PIPELINE LAYING / INSTALLATION in all type of surface (Normal/built-up surface) "Receiving and taking over" as defined in the specifications, handing, loading, transportation and unloading of Owner supplied 3-Layer PE coated linepipes from Owner's designated stack-yard to Contractor's stock yard/workshop/work-site including preliminary activities, preparation of drawings, wherever required for crossing etc. including handling, stacking, stringing on the pipeline Right-of-Use/ pipeline route alignment, carrying out inspection of company supplied materials including linepipes at the time of taking over, laying/ installation of coated linepipes, associated burried valves, barred tees, insulating joints, flanges & fittings of all sizes, thickness & ANSI class rating and accessories as per specification wherever required depending on site condition including execution of all works, "taking over", handling , including loading and unloading, transportation of Owner supplied materials other than linepipe from Owner's designated place (s) of issue to work site, | Item2 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3 | additional lands required for Contractor's storage, fabrication, access for construction, procurement and supply of all materials (except Owner supplied materials), consumables, equipment, labour and other inputs, carrying out all temporary, ancillary, auxiliary works, aquistion of ROU/ROW for laying of pipeline from HDD Exit and entry point to Tie in Point of existing Pipeline/ ROU, ready for commissioning of pipeline as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge, including but not limited to carrying out the following works: | Item3 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4 | Surveying of route and detours required at the time of execution including marking the same in topographical sheet, preparation of construction drawings showing survey details, and submit same to Owner for review / approval. | Item4
5 | Staking and installation of construction markers, clearing, fencing, grubbing, cutting of trees, full filling all the requirements of various statutory/ environment authorities to the entire satisfaction of concerned authorities, grading of work area. Shifting of all obstruction within the ROU/ Pipeline route alignment viz. electrical lines/ poles, telephone line / poles, etc. coordination with concerned authorities and obtain permissions from these authorities. | Item5
6 | Trenching to all depths by excavation in all types of soils including soft/ hard rock and different type of pavement / footpath / roads etc. including rock breaking, chiselling or otherwise cutting etc. as required and storing excavated soil, reusable materials at designated area as directed by Engineer in charge and to a width to accommodate the Steel pipeline and MDPE as per the relevant standard/ specification etc. [The minimum depth of the top of pipeline shall be 1.2m measured from top of pipeline coating to the top of undisturbed surface of the soil or as per SCC/ OISD - 141 / 226, whichever is higher]. Dewater of trenches if required as per site condition. | Item6
7 | Carrying out repairs of pipe defects/ replacement in case of irreparable defects and repairs of defects of pipe coating not attributable to Owner including defects/ damages occurring during transportation / handling. | Item7
8 | Stringing of line pipes along pipeline trench / ROU on straw / sand / soft soil bags including supply of bags and its filling materials. | Item8
9 | Checking, cleaning, aligning, bending, cutting and bevelling (as required) of pipes for welding and field adjustments including pipe fittings, welding, carrying out non-destructive testing of welds as required including 100% radiography by X-ray and providing all requisite equipment, labour, supervision, materials, films, consumables, all facilities and personnel to process, develop, examine and interpret radiographs and other tests as required, carrying out repairs of weld joints found defective by Engineer-in-Charge, carrying out re-radiography and other tests as required on repaired joints. | Item9
10 | Carrying out installation of carrier line pipe at all minor crossing viz. carttrack, pathway etc. at designated depth by open cut (except at crossing/Laying along the road by HDD method). | Item10
11 | Carrying out installation of carrier line pipe in the casing pipe at cased crossing (excluding installation of casing pipes which is covered separately). | Item11
12 | Coating of field weld joints, long radius bends (R=3D), elbows, buried fittings and valves etc. including supply of coating materials etc. (i.e. heat shrinkable sleeves and high build epoxy etc.) as per PJS & Technical Specification compatible with 3 layer PE coating material of the line pipe. | Item12 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
13 | Counting the number and type of trees cut in presence of DFO/concerned authorities and keeping record thereof, stacking and handing over of all cut tress. | Item13
14 | Installation / lowering the pipeline in trench to required depth as per PJS, Techanical Specification & drawings, supply & placement of 1.0mm thk. HDPE Yellow colour warning mat,RCC tiles (300 mm width x 50 mm thick) over the pipeline & MDPE Pipe in same trench along the complete route as per standard drawings, data sheets & technical specifications, padding around pipeline as per Standard Drg. no. MNGL/Plng./Steel/03 with suitable soil duly approved by EIC including supply of padding material, backfilling and its compaction to the satisfaction of concerned authorities with excavated earth / borrowed select soil including supply of borrowed select soil duly approved by EIC before backfilling and make ready for restoration to be done by Onwer / concerned authorities. | Item14
15 | Supply and installation of slope breakers, wherever required or, as directed by Onwer / Engineer–in–charge. | Item15
16 | Crossing the all-foreign pipeline / HT line / cable / any other utilities etc. with necessary concrete / HDPE sheet protection including coordination with all agencies and obtaining NOC | Item16
17 | Supply and installation of bank protection alongwith backfill materials duly approved by EIC for pipeline trench and banks falls under minor water body crossing as per technical specification & Std. Drg. No. MNGL/Plng./Steel/28, wherever required or, as directed by Onwer / EIC. | Item17
18 | Training and diversions of streams in steep slope area, wherever required. | Item18
19 | Carrying out air cleaning, pigging, flushing, cleaning and hydrostatic testing of complete pipeline with required quantity of corrosion inhibitor including pre-testing of designated sections complete as per specification and approved by Engineer–in–charge to specified pressures indicated elsewhere and duration after stabilization as per specification, providing all equipment, pumps, fittings, instruments, dead weight tester, pressure recorder, thermocouples etc., and services, supervision, labour, consumables, water including supply of corrosion inhibitor, air, etc. as required, locating of leaks and rectification of defect attributable to Contractor (rectification of defects in linepipe material not attributable to contractor shall be paid separately as per other item of schedule of rate), re-testing after rectification, dewatering after successful completion of hydrotesting of entire section and as per specification | Item19
20 | All tieing-in, including the tie-in(s) of the pipeline with the adjacent sections of pipeline including cutting of test header, rebevelling as required, radiography and other NDT examination, joint coating as per specification. | Item20
21 | Final clean-up of right-of-use or area disturbed by contractor during their construction activities for laying of pipeline works and disposal of debris and surplus material to designated disposal areas and backfilling of trench and compaction of the same as per satisfaction of Owner and / Or as directed by Engineer–in–charge. | Item21
22 | Installation of all burried valves (except extended stem valves) inside the valve pit and making provision to operate the valve. | Item22 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
23 | Preparation of as-built drawings, pipe-books (1 set of tracing on polyester film and 6 sets of as-built drawings and 1 soft copy and 6 hard copies of pipe book) All the works shall be executed in accordance with the provision of contract including carrying out all temporary/ ancillary/ auxiliary works required for the performance of the works and all other acts, deeds, matters and things necessary to make the pipeline ready for precommissioning activities. | Item23 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
24 | Raking up of hard surface of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. Payment for cutting of hard rock, if any, is covered unders SOR no. 77 | Item24 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
25 | Specified dia Thk (mm) Material Coating Type Length of each pipe (mm) NB | Item25 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
26 | 10" NB W.T 6.4mm API 5L X-70, 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item26 | 5000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
27 | Note: This item shall be applicable for the underground steel grid main pipeline & branch pipeline, barred tees, insulating joints, bends, flanges & fittings, accessories etc. (i.e. including arrangement for making provision for tap-off on proposed steel grid main pipeline) and aboveground approach pipeline upto Insulating Joint (excluding installation of aboveground insulating joint) for various stations. | Item27
28 | In above item, restoration works are excluded from contractor's scope, except certain restoration works detailed in clause no. 16C. (V) of 3a. Particular Job Specification under Vol.-I of III. Since restoration works for backfilled pipeline trench shall be done by the concerned authorities / Owner. | Item28 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
29 | In above item, backfilling of pipeline trench by borrowed soil duly approved by Owner / EIC shall be paid by separate item mentioned elsewhere in the SOR. | Item29 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
30 | Items except above are covered separately. The lengths of pipelines are tentative. | Item30 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
31 | Permission Liasioning /Follow-up | Item31 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
32 | Liasioning & follow up for Permission with all the concerned authorities & boards viz Railways, NH, PWD, MIDC, Local Municipal, Panchyat, Electricity, REC, RES, Sewage water, Drinking water, Forest, Social Forestry, Owners of OFC, Traffic, Law & Order, Fire Brigade, Private Land Owner etc. for entire pipeline length and associated terminals (like SVs, tap-offs) alongwith associated work as per tender. Obtaining necessary NOC from authority after completion of work (Where ever applicable). | Item32 | 5000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
33 | Laying of RCC Tiles | Item33 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
34 | Providing single layer of RCC Tiles with supply of RCC Tiles to entire width of trench above Warning Mat placed in trench over the laid pipeline as per standard drawing, specification and instruction of Owner. (Rate to include cost of all labour, tools, tackles, equipment, hire charges & supply of all materials, etc.) | Item34 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
35 | For width of 10" pipeline trench | Item35 | 5000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
36 | Barricading to comply with HSSE | Item36 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
37 | Steel barricading of the trenches Cautionary Sign Boards and lighting arrangement shall be provided as per attched drawing no.MNGL/Plng./steel/04. The rates include barricading of trenches along with sign boards, lighting etc. and maintain the same till the back filling of the trench. Rates will be payable per metre of BARRICADING PROVIDED. If proper barricading is not provided, MNGL will barricade the trenches at the risks and costs of the CONTRACTOR and will levy penalty of twice the rate per unit for the relevant section of the pipeline apart from other actions as per contract. | Item37 | 5000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
38 | RESTORATION OF ROADS Restoration of asphalt / concrete / red stone roads / pavement/Footpath/Paver block including compaction of soil, to original condition as per requirement and to the entire satisfaction of EIC and / or concerned Owners having jurisdiction for following thickness. | Item38 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
39 | Restoration of Asphalt road upto 10 cm thickness | Item39 | 400 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
40 | Restoration of Asphalt road beyond 10 cm upto 20 cm thickness | Item40 | 300 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
41 | Restoration of Concrete road upto 10 cm thickness | Item41 | 1000 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
42 | Restoration of red stone road / footpath / pavement/ Paverblock upto 4 cm thickness | Item42 | 1200 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
43 | BORROWED SELECT SOIL FOR BACKFILLING Additional work over and above item 1.0 for supply of specified and approved quality of borrowed soft graded soil / sand in place of available excavated material and / or other suitable soil as per applicable standards / specifications, including backfilling of excavated trench for specified length after laying and padding of pipeline, including transportation of such special backfill material over all distances, complete. | Item43 | 900 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
44 | CROSSING OF STEEL PIPELINE BY OPEN CUT | Item44 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
45 | Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insatllation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed. | Item45 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
46 | Road Crossing By Open Cut Method Road Crossings at various locations by Open cut Method along with laying of MDPE upto 180 mm Dia if necessary as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item46 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
47 | Line pipe detail 10" NB, 6.4 mm thk API X-70 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item47 | 110 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
48 | Water body Crossing By Open Cut Method kulvert/ canal/ nallah/ drain/ channel Crossings at various locations by Open cut Method along with laying of MDPE upto 180 mm Dia if necessary as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item48
49 | Line pipe detail 10" NB, 6.4 mm thk API X-70 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item49 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
50 | Note: Laying of the pipeline by the approved method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item50 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
51 | Backfilling of the Road/water/ canal/ nallah/ drain/ channel Crossings/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority. | Item51
52 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item52
53 | CROSSINGS/LAYING ALONG THE ROAD BY HDD METHOD | Item53 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
54 | Complete work of the any crossing (between the limits are defined as approved drawings) by HDD method including "Receiving and taking over" owner supplied three layer PE coated line pipes from Owner's designated place to issue/ dump site(s) and transportation to Contractor's stock yard/ work shop/ work site including all handling loading, unloading, aligning etc. supply of all Contractor supplied material, manpower, equipment, other resources and aquiring the required land for storage, fabrication inclduing string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type Heat Shrink Sleeve and repair of pipeline coating with special repair patch materials as per specification,pre-testing etc. of complete string made for crossing access for Contractor etc and execution of, but not limited to, following works in accordance with specifications scope of work and instructions of Engineer-in-charge and as per all provision of Contract Document. | Item54 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
55 | Pre-construction surveys based on site visit, collection of historical data from irrigation/ concerned department including design & calculation and detail engineering and making of crossing drawing for getting their approval from concerned Authority/ Engineer-in-charge, getting work permit/ NOC for water crossings/ road crossings as well as utility crossings (if any) encountered during crossing prior to start the execution of work. | Item55 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
56 | Directional drilling to required depth from top of road including maintenance of drill hole in all types of strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) at all depth to accommodate the pipeline at all conditions encountered during rail/ road crossing by approved HDD methods for providing minimum cover specified in code/ specification or the actual depth as decided by concerned authority, whichever is more. | Item56 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
57 | In case of water crossing, drilling to the required depth on the banks and bed including maintenance of drill hole in all types of soil strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) all depth to accommodate the pipeline a by HDD methods for providing with minimum cover over top of the pipe at all point across the maximum possible width of water bed (as per drawing) either 1.5 mtrs. below the predicted scour profile expected during the life time of the pipeline or 2.5 mtrs. below the available lowest firm bed (if scour profile/ depth not available) of the water crossing by ascertaining bed level upto 50 mtrs. both the side from crossing location or the actual depth as decided by concerned Authority/ Engineer-in-charge whichever is more. | Item57 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
58 | Laying of the pipeline by the approved HDD method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints with special type Dirax Heat Shrink Sleeve or equivalent and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item58 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
59 | Backfilling of the ditch/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority and all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specification, approved drawings, calculations, methods and to the satisfaction of Engineer-in-charge and/or as directed by concerned Authority. | Item59 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
60 | Post installation hydrotest dewatering and tie-in with pipeline at either side of crossing/banks etc. | Item60 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
61 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item61
62 | Crossing of Road/Drain/channel/Nallah/River crossings by carrier pipeline of size 250 mm NB x 6.4 mm thk. of API X-70 (along with laying of 4'' Steel Pipe for MDPE if necessary) by HDD Method | Item62 | 70 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
63 | Laying along the Road by carrier pipeline of size 250 mm NB x 6.4 mm thk. of API X-70 (along with laying of 4'' Steel Pipe for MDPE if necessary) by HDD Method | Item63 | 70 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
64 | Installation of carrier pipes by rock drilling for along the road/Drain/Canal/Channel Crossing/Nallah, or wherever required in all types of hard rock. It includes survey of the underground utilities, submission of profile for approval, execution of the work as per the standard procedure, including , excavation of the pits, insertion/pulling of the carrier pipe, removal of malba, subsequent backfilling and restoration of the facility crossed as per original condition, including supply of all other materials, equipment, consumables, manpower etc including string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type of Heat Shrink Sleeve (Direx) and repair of pipeline coating with special repair patch materials as per Specification, pre-testing etc. of complete string made for crossing/ laying access for Contractor etc. and execution of, but not limited to, following works in accordance with specifications and instruction of Engineer-in-Charge and as per all provision of Contract Document. Balance activities as defined in SOR Item of open trench. Note:The length of HDD mentioned is tentative and may vary to the considerable extent depending upon requirements as per site conditions. The length mentioned in SOR is indicative for all the crossing to be done by HDD, numbers and locations shall be decided by Engineer-in-Charge depending upon site condition. Payment for the length of final tie-in carrier pipeline string with mainline laid by HDD are inclusive in this above item rate. No separate payment shall be made under other clauses mentioned elsewhere. Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item64
65 | Crossing of Road/Drain/Canal/Channel/Nallah/River Crossing crossings by carrier pipeline of size 250 mm NB x 6.4 mm thk. of API X-70 (along with laying of 4'' Steel Pipe for MDPE if necessary) by HDD Method | Item65 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
66 | Laying along the road by carrier pipeline of size 250 mm NB x 6.4 mm thk. of API X-70 (along with laying of 4'' Steel Pipe for MDPE if necessary) by HDD Method | Item66 | 60 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
67 | Note: (i) Crossing width & Actual string length for HDD shall vary as per design calculations & site condition so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. | Item67
68 | (ii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by HDD method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item68
69 | (iii) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossing at different locations. | Item69
70 | (iv) The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. | Item70
71 | Note: (i) Quantity mentioned under item nos. 4 are indicative only for different location of River/roads/water/ canal/ nallah/ drain/ channel Crossings. (ii) Actual length & width of individual crossing and cover from top of casing pipe/ carrier pipe string may vary depending upon site condition, approved crossing drawings, specifications etc. and / or as decided by Engineer-in-charge/ Concerned Authority. | Item71
72 | (iii) Payment for supply & installation of Zinc ribbon anode and its design excluded from above item and covered elsewhere in the SOR. (iv) Payment for the length carrier pipeline string inserted in casing pipe laid by Boring are covered separately and shall be paid under other clauses mentioned elesewhere in the SOR. | Item72 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
73 | Excavation beyond 1.5m depth in case of crossing of utilities/ drain/ culverts etc. through open cut upto the following depth (including restoration of the damaged area to its original condition and satisfaction of the Engineer-in-charge / concerned authorities) : - | Item73
74 | In all type of surface (Normal/built-up surface) of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. The other activities are as per SOR 1.1. Payment for cutting of hard rock, if any, is covered unders SOR no. 77 | Item74
75 | Deeper than 1.5 m & upto 2.5 m below existing level (for 250 (approx.) mm NB Pipeline) | Item75 | 1200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
76 | Deeper than 2.5 m below existing level (for 250 (approx.) mm NB Pipeline) | Item76 | 400 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
77 | Excavation of hard rock | Item77
78 | Excavation of hard rock wherever hard rock of single piece exceeding 1.0 m in length removable by pneumatic chisel/ drill as per direction of EIC. | Item78 | 3500 | Cub. M |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
79 | REPAIR OF COATING DEFECTS (NOT ATTRIBUTED TO CONTRACTOR) | Item79
80 | Repair of Holiday in Coating (Noted and recorded at the time of "receiving and taking over") Supply of all coating repair materials as per requirements of specification to be compatible with line pipe coating material, supply of all consumables, utilities, equipments and all manpower required, pipe cleaning and surface preparation, repairing of coating defects (resulting in holiday) and testing including all handling, transportation, etc. for line pipes, performing all works necessary for the completion of the works stirctly in accordance with relevant specification and instructions of Engineer-In-Charge. This rate shall be applicable per sq. cm of the exposed steel area exposed steel area. | Item80 | 2000 | Sq. cm. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
81 | PERMANENT MARKERS Supply, fabrication and installation of all types of permanent markers along the route including all associated civil works such as excavation in all types of soil, construction in all types of soil, construction of pedestals and grouting with concrete, clearing, supply and application of approved colour and quality of primer and paint, stencil letter cutting for numbers, direction, change etc., restoration of area to original condition and performing all works as per drawing, specification and instruction of engineer-in-charge. | Item81 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
82 | Pipeline RCC boundary / route marker as per drawing | Item82 | 100 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
83 | Pipeline warning markers with post & foundations | Item83 | 35 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
84 | Pipeline direction marker with post & foundations | Item84 | 28 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
85 | Pipeline KM with post & foundations | Item85 | 5 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
86 | HOOK -UP | Item86
87 | Hook-up of proposed pipeline by welding of final tie-in-joint with any existing laid pipeline portion of river X-ing ,existing Tap-off & battery limit of Section I & II including Hook-up point of the existing pipeline to be made ready for welding by cutting of flanges / valves / headers at all depth in all type of soil etc. Venting of N2 / gas / gas mixture as required purging of N2 Gas (if required), rebevelling as required, radiography and other NDT examination, joint coating as per specification.Contractor shall supply of all consumables, manpower, machinaries, materials, N2 gas etc. and carry out all works as per the provisions of Contract document and instructions of Engineer-in-charge. | Item87 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
88 | For 10" NB 600 # | Item88 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
89 | PRE-COMMISSIONING AND ASSISTANCE IN COMMISSIONING OF PIPELINE SYSTEM Swabbing, drying, purging with nitrogen of the complete pipeline network and the associated facilities being installed to the specified acceptance criteria, carrying out pre-commissioning works, providing assistance during the complete duration of commissioning operations for entire pipeline network system including supply of all equipment, man-power, consumables (including pigs & nitrogen required for purging with maintaining nitrogen column of mininum 10% of pipeline geometric volume) materials for all temporary works and performing all associated works, complete as per the relevant specifications, other provisions of Contract document and instructions of Engineer-in-charge. | Item89 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
90 | For 10" NB 600 # | Item90 | 5000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
91 | IDLE TIME PRESERVATION OF PIPELINE Preservation of complete pipeline and associated facilities forming part of the pipeline as per Bid document and its maintenance including supply of all consumables, all equipment, manpower, etc. complete as per the requirements of specifications, other provisions of Contract document and instructions of Engineer-in-charge. Note : Owner reserves the right to exercise either or none of the rates below. | Item91 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
92 | By filling and pressurizing with nitrogen to a pressure of 2 bar(g) for a period of 3 months. | Item92 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
93 | For 10" NB 600 # | Item93 | 5000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
94 | For every additional period of one month or part thereof | Item94 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
95 | For 10" NB 600 # | Item95 | 5000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
96 | RCC VALVE PITS All civil works including supply of all materials, excavation of pit, piping supports including all PCC and RCC works for valves pits including pedestals with insert plates as required sealing of pipe at valve pits, providing cover etc. and finishing , clean-up and restoration of site, filling and grading of area around valve station for avoiding any local flooding of area, as per typical drawing and specification enclosed and instructions of Engineer-in-charge. In this item, instead of Brick Work, RCC will be done | Item96 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
97 | Valve Pit of Size 2m x 2m | Item97 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
98 | Valve Pit of Size 1 m x 1 m | Item98 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
99 | SUPPLY OF ASSORTED PIPE, FITTINGS AND FLANGES Complete works of supply of pipes, flanges & fittings for aboveground & underground installation including all taxes, duties, transportation and inspection charges but not limited to, the following items in accordance with PMS (piping material specification), relevant specifications & drawings indicated in job specification under SCC (technical) and instructions of Engineer-in-charge and as per all provisions of the CONTRACT DOCUMENT. - Handling including lifting, transportation from Contractor Stores to CONTRACTOR's workshop for fabrication and/ or to work site for field fabrication and erection for all piping items supplied by Contractor. | Item99 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
100 | Carbon Steel Pipe (A 106, Seamless B-36.10/ API X 70 ) | Item100 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
101 | Size Rating/ Schedule | Item101 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
102 | 2" NB, BE Sch. 80 | Item102 | 38 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
103 | 1" NB, PE Sch. 80 | Item103 | 36 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
104 | ¾" NB, PE Sch. 160 | Item104 | 30 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
105 | Flanges | Item105 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
106 | Weld Neck (B-16.5, 600# A105,125 AARH, Serrated finish) | Item106 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
107 | Size Rating/ Schedule | Item107
108 | 2" NB, RF End thickness to match with pipe wall thickness (SCH 80) | Item108 | 15 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
109 | Blind Flanges (B-16.5, 600# A105,125 AARH Serrated) | Item109 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
110 | Size | Item110 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
111 | 2" NB, RF | Item111 | 15 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
112 | Elbow (Seamless) | Item112
113 | 90° Elbow (MOC MSS SP 75 WPHY 70 R= 3D ) Min Thickness 6.4mm | Item113 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
114 | Size Rating/ Schedule | Item114 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
115 | 10" NB 600# | Item115 | 25 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
116 | 45° Elbow (MOC MSS SP 75 WPHY 70 R= 3D ) Min Thickness 6.4mm | Item116 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
117 | Size Rating/ Schedule | Item117 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
118 | 10" NB 600# | Item118 | 25 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
119 | 22½° Elbow (MOC MSS SP 75 WPHY 70 R= 3D ) Min Thickness 6.4mm | Item119
120 | Size Rating/ Schedule | Item120
121 | 10" NB 600# | Item121 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
122 | 11½° Elbow (MOC MSS SP 75 WPHY 70 R= 3D ) Min Thickness 6.4mm | Item122 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
123 | Size Rating/ Schedule | Item123 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
124 | 10" NB 600# | Item124 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
125 | Tees (Seamless) | Item125
126 | Equal Tee (MOC MSS SP 75 WPHY 70 & DIM. ASME B16.9) | Item126
127 | Size Rating/ Schedule | Item127
128 | 10" NB x 10" NB x 10" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item128 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
129 | 2" NB x 2" NB x 2" NB Sch. XS | Item129 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
130 | Reducer (MOC MSS SP 75 WPHY 70 & DIM. ASME B16.9) | Item130
131 | 10" NB x 6" NB Min Thickness 6.4mm | Item131 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
132 | 10" NB x 4" NB Min Thickness 6.4mm | Item132 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
133 | 12" NB X 10" NB Min Thickness 6.4mm | Item133 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
134 | 4" NB X 2" NB Min Thickness 6.4mm | Item134 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
135 | 10" NB X 8" NB Min Thickness 6.4mm | Item135 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
136 | Weldolet and Sockolet | Item136
137 | Weldolet (MOC A105 & DIM. MSS SP 97) | Item137
138 | Size Rating/ Schedule | Item138
139 | 10" NB x 2" NB Sch. 80. (600#) | Item139 | 10 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
140 | Sockolet (MOC A105 & DIM. MSS SP 97) | Item140
141 | 10" NB x 3/4" NB 600 # | Item141 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
142 | Butt Weld Disc End Cap (MOC MSS SP 75 WPHY 70 & DIM. ASME B16.9) | Item142 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
143 | Size Rating/ Schedule | Item143 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
144 | 10" 600 # | Item144 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
145 | Fabrication & Installation of Underground Valve Assembly (including Pneumatic testing of Assembly before installation at Design Pressure) | Item145 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
146 | 10"NB Isolation Valve/tap-off assembly as per Drg. No. MNGL/Plng./Steel/40 | Item146 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
147 | Note: | Item147
148 | For all the supply items mentioned above, procurement shall be made as per enclosed Data Sheets and respective technical specification, after due approval of Engineer-in-charge. | Item148 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
149 | The quantities mentioned above are tentative and quantities for above supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item149 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
150 | OFC | Item150 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
151 | Supply of 24 Fibre Composite armored Optical Fibre Cable drum (24 Fibres as per ITU-T G652D) of 5 km +/-5% Cable drum length with, Two number electronic locater as per PTS-Optical Fibre cable. | Item151 | 5000 | M |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
152 | Supply of 40 MM Permanently Lubricated HDPE duct along with all the required accessories | Item152 | 5000 | M |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
153 | Laying of HDPE duct with Steel Pipeline | Item153 | 5000 | M |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
154 | Blowing of Optical Fibre Cable inside HDPE Duct/conduit | Item154 | 5000 | M |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
155 | Supply and Installation of Inspection chamber | Item155 | 5 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
156 | Supply & Installation of Electronic marker | Item156 | 5 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
157 | Splicing, Jointing of optical fiber cable , final Jointing / splicing, Testing of OFC after jointing all completed as per specifications | Item157 | 5 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
158 | PLANT PIPING (ABOVEGROUND) Fabrication and testing of carbon steel piping and fittings, valves, IJ, including supply of all consumables, equipment, manpower, and other resources and execution of job as per instruction AIC/EIC.Transportation of all piping items from Owner's and/ or Contractor's storage point to work at site/ workshop as applicable, complete work of fabrication, erection, painting, testing of pipes, flanges and fittings and making ready for further Commissioning / Start-up of carbon steel piping of all sizes and ratings including supply of all consumables, equipment, manpower and other resources and execution of, but not limited to, the following works in accordance with relevant specifications indicated in item 99 of PJS & scope of work indicated in SCC, drawings, specification and instructions of Engineer-in-charge and as per all provisions of the CONTRACT DOCUMENT. | Item158 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
159 | Fabrication including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site, cutting, edge preparation, inclusive of grinding the edges of pipes, fittings, flanges, reducers etc. to match with the matching edges of uneven thickness, wherever required, fit-up, welding of pipes and fittings like elbows, tees, reducers, weldolets, sockolets, Valves, IJ etc. flanges, vent and drain point connection, Radiography and NDT of all joints etc, including providing stubin connections, fabricated fittings and reinforcement pads etc., as required. | Item159 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
160 | Erection of pipes of all types and thickness at all elevations, connecting with equipment nozzle, aligning, installation and carrying out connected activities for all types of valves, all online instruments and fittings of all sizes of elbow, reducers, tees, flanges, blind flanges, spectacle blind flanges, branch connection / tapping for pressure gauges, including installation of gaskets and bolts. | Item160 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
161 | Erection including prior cleaning, lifting, placing on pipe sleepers and supports, overhead on racks, skids and at all elevations including installation and carrying out connected activities for all types of valves including supply and fixing of gaskets, studs/ bolts, nuts wherever required for all sizes, levelling, aligning, joining of flanges, blind flanges, connecting with equipment, nozzles, strainers, tie-in with existing piping/facilities, etc. tapping for inline instruments like pressure gauges, thermowells, sample connection, etc. | Item161 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
162 | Hydro testing of the piping job shall be conducted at pressure mentioned in specification for a period of 4 hours by using de-mineralised water, to check its strength. No visible leakages shall be detected during the test. Testing shall be conducted as per tender specification.Pneumatic Testing of entire above ground piping at Design pressure before final hook up. | Item162 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
163 | Preparation of final bill of material based on piping GADs. | Item163 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
164 | Preparation of isometric and fabrication drawings. | Item164 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
165 | Carrying out Non-destructive testing as required except items mentioned in sl. no. 223 of SOR. | Item165 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
166 | Painting of entire system (including aboveground all pipes fittings, flanges and accessories) as per specifications suitable for highly corrosive area environment including supply of approved paints and primers, application of primer and paints, indentification lettering/ numbering, colour coding, etc. as specified including rub down & touch up of shop primer or scrapping of shop primer wherever required by COMPANY and providing scaffolding for all heights etc. | Item166 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
167 | Cleaning and flushing by water/ compressed air, testing of the systems including hydrostatic, pneumatic and any other type of testing as specified, draining, drying by compressed air/other methods approved by COMPANY. | Item167 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
168 | Precommissioning & making operational all piping system and equipments. | Item168 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
169 | Commissioning Contractor scope shall provide all necessary assistance in term of supply of man-power, equipment, tools and tackles required amount of nitrogen for purging of entire terminal piping system including equipments etc. to the company during commissioning activities. | Item169 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
170 | Completion of all such work in all respects as per scope of work and as per drawings, specifications and instructions of the COMPANY and keeping the system ready in all respects for further commissioning and start up. | Item170 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
171 | Hook-up works (with client/ consumer piping at battery limits): | Item171 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
172 | Complete Carbon Steel aboveground Piping Work with painting including all fittings, flanges and supply of all required gaskets, studs bolts & nuts etc., and Any other work and material required for the completion of the work and not covered above and desired by EIC shall be in the scope of contractor | Item172 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
173 | Carbon Steel Pipe (ASTM A 106, Seamless B-36.10 / API X 70) | Item173 | 500 | inch Dia |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
174 | 1) Pipe Specification and thickness may vary depending upon availability of pipe. No extra payment shall be made for this. 2) All butt welded fittings & flanges end shall generally match with connecting pipe wall thickness. However, in case of misalignment, Contractor shall have to do end preparation without any extra cost. 3) All o-lets less than 2" NB size, all sizes of coupling and nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under erection rate. | Item174 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
175 | Aboveground installation of Insulating Joint & Valves etc. Handling including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site and installation of all types of valves, insulating joint including assembly of valve accessories, (if any) by bolting, threading or welding, supply and insertion of gaskets, nuts & bolts, nipples, etc. at all elevations of pipe sleepers, supports or overhead on racks, equipments nozzle, skid & painting etc. supply of all consumables, manpower, equipment, etc. for completion of all works as per scope of work and as per drawings, specifications and instructions of Engineer-in-charge including servicing/ cleaning of valve wherever requried. | Item175
176 | Welded Valves (Full Bore/ Reduced Bore) Ball / Globe / Check Valve | Item176
177 | Size Rating/ Schedule | Item177
178 | 10" NB 600# | Item178 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
179 | 2" NB 600# | Item179 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
180 | Sockolet Welded Valve (Ball / Globe Valve) | Item180
181 | Size Rating/ Schedule | Item181
182 | 1" NB 800# | Item182 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
183 | ¾" NB 800# | Item183 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
184 | Insulating Joints | Item184 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
185 | 10" NB, 600# - Insulating Joints | Item185 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
186 | STRUCTURAL WORKS | Item186 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
187 | Supply of erection of single leaf mild steel gate 2.5m high with mesh upto 2m height and barbed wire fencing and 2m wide complete in all respect including painting as per TS on all MS items, all works as per specification and drawings excluding foundations and RCC beams. | Item187 | 10 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
188 | Supply of all materials, fabrication and erection of chain link fencing 2.5m high with mesh up to 2m height and barbed wire fenching complete in all respects including painting as per TS on all MS items, all works as per specification and drawings excluding foundation and RCC beams. | Item188 | 150 | RM |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
189 | Pipe Supports & Other Structures | Item189 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
190 | Supply, fabrication and erection of all types of pipe supports like clamps, saddle, guide stops, cradles, turn buckles, anchors, T-posts; stockade/ trestle and pipe bridge for overhead piping; frames for canopy, approach ladders and platforms, crossover, cable tray supports, etc. including painting suitable for highly corrosive area as per specification labour and supervision & complete work as per drawings, specifications and instruction of Engineer-incharge. (Bolts, nuts, washers, U-clamps etc. for supporting shall be supplied by the Contractor within the rates quoted. These items will not be measured and paid seperately). The work is to be completed in all respect as per scope of work and specification. | Item190 | 300 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
191 | Notes: | Item191 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
192 | The quantities indicated are estimated values and hence are approximate. Final payment will be made based on actual quantities to be certified by the Purchaser. | Item192 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
193 | The cost of MS bolts (permanent and service(, washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants etc., as required for the work shall be deemed to be included in the quoted rates. | Item193 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
194 | All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accrodance with time schedule, are deemed be included in the quoted rates. | Item194 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
195 | CIVIL WORKS | Item195 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
196 | Site Grading Excavation in earth and filling to the grades and levels shown in the approved drawings in all kinds of conditions including for Road embarkments, using approved quality good earth from designated borrow area, for all heights and depths including clearing and stripping (min. 150mm) of the area marked for filling, taking spot levels, consolidating the exposed natural soil surface, excavating the earth from borrow area loading, transporting & unloading, spreading in layers not exceeding 150mm thickness, breaking clods, watering (if reqd.), ramming and compacting by manual/ mechanical means to give minimum 92% of modified Proctor's density of earth, testing & dressing including disposal of all unserviceable material all complete as per specifications and directions of Engineer-in-charge. | Item196 | 200 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
197 | (Rate to include cost of all labour, tools, tackles, equipment, hire charges, cost of borrow earth by way of royalties, right of way, cess etc., as applicable with all bye works and sundry works). | Item197
198 | Plain Cement Concrete Supplying and laying plain cement concrete (including shuttering of required) in all types of concrete works including levelling courses below foundation, substructure, superstrcuture, chambers, cable tranch, under floors and any other locations, at all leveies as per drawings, specifications and directions of the Engineer-in-charge. | Item198
199 | PCC 1:2:4 1 Cement : 2 Coarse sand : 4 stone aggregate 20mm nominal size. | Item199 | 250 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
200 | Reinforced Cement Concrete Providing and laying reinforced cement of grade M-20 with 20mm and down grade crushed stone aggregate in all types of structures like foundations, pedestals, pedestal bases, pipe supports, sleepers cable trench inlcuding constrcution joints, bitumen painting on surface in contact with soil, providing and fixing reinforcing steel, shuttering, inserts, finishes etc. at all depths and heights complete as per drawings, specifications and direction of the Engineer-incharge. | Item200 | 400 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE!
201 | Rate to include cost of all labour, tools, tackles, equipment, hire charges, supply of all maerials such as minimum 43 grade cement including sulphate resistant cement for substructures, R/F steel, Inserts, bolts, conduits, bitumen, other minor constrcution materials, shuttering, stanging, earthwork in excavation and backfilling using serviceable earth in all conditions, shorting bailing and pumping out water, testing of concrete, curing etc. with all bye works and syndry works. | Item201
202 | TEMPORARY CATHODIC PROTECTION SYSTEM | Item202
203 | Design, detailed engineering, supply, installation, testing and commissioning of the temporary Cathodic protection system using Mg/ Zn galvanic anodes to protect the external surface of 3 LPE coated entire 5.5 (approx.) long steel pipeline network against corrosion for design life of minimum 1 year or till commissioning of PCP system whichever is later as per standard specification No. MNGL/Steel/TS/15 for temporary cathodic protection system. Scope shall also include but not limited to the following for completion of jobs: | Item203
204 | Measurement of soil resistivity along the right of way of the main pipeline route as per specification for design & installation of anodes. | Item204
205 | Collection of additional data related to cathodic protection along the right of way of pipeline as per specifications. | Item205 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
206 | Supply, installation, testing & commissioning of one set of spark gap arrestor with 2 plate Zinc grounding cell of 20 kg net weight each across each insulating joint as per specification. | Item206 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
207 | Supply, installation, testing & commissioning one set of polarisation cell with zinc anode at all high tension (66KV or higher) electrical power transmission line/Equipment crossing or running parallel to the pipeline for grounding purpose as per specification. The rating shall depend upon anticipated fault current & ground bed resistance at the location of installation. However, the rating of polarisation cell (krick) shall not be less than 5 KA & number of 20 kg net weight zinc anode shall not be less than two. | Item207 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
208 | Supply & installation of Zinc Ribbon Anodes at 4-8 O’Clock position in the interval of 2 metre (max.) on carrier pipes at all cased crossings i.e. railways/ roads etc. | Item208 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
209 | Monitoring of the protection system for 6 months. | Item209 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
210 | All civil/ structural works related to TCP system including supply of bricks, cement & steel etc. required for completion of the system. | Item210 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
211 | For 10" | Item211 | 5000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
212 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item212 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
213 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item213 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
214 | FIELD INSTRUMENTATION | Item214
215 | PRESSURE INSTRUMENTS | Item215 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
216 | Supply , Installation of Pressure Gagues and their accessories inclusive of supply of necessary piping materials and tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/ manifolds & hydraulic testing (exclusive of calibration of instruments) as per installation standard attached elsewhere in Tender Document and Supply as per Data Sheet No.MEC/23K8/05/E5/I/001/DS-PG. Give breakup of supply and Installation rate. | Item216 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
217 | CALIBRATION | Item217
218 | Calibration of the instruments listed below including removal of instruments from pre-installed locations like panels, enclosure racks, fields etc. and refixing them back in respective/ required places, providing equipments, necessary test jigs, instrument air and all consumables. Calibration reports shall be prepared and to be submitted to the Purchaser/ Consultant. | Item218 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
219 | Pressure Gauges | Item219 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
220 | Note: | Item220
221 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item221 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
222 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item222 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
223 | Laying of MDPE pipe along with Steel pipe line Excluding supply of all MDPE pipe (PE 80/100,SDR11), but Including supply of Bends, Couplers, End caps, Tees, PE Reducer, CS to PE Fitting, Saddle Tapping, Warming mat, etc. as required to complete the job. ( Particular job specification.) "Receiving and taking-over" as defined in the specification, handling, loading, transportation and unloading of Owner supplied MDPE line pipes (PE80/100, SDR11) of all sizes (as free issue items) from Owner's designated place(s) of issue to Contractor's own stock-yard(s)/ Work Shop(s)/ work-site(s) including proper storing, stacking, identification, providing security & insurance cover , including supply of accessories of all sizes & thickness like Bends, Couplers, End caps, Tee, PE Reducer, CS to PE Fittings, Saddle Tapping, Warning Mat, etc.. | Item223 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
224 | Stringing/ uncoiling of the MDPE line pipe on the pipeline Right-of-Use, laying/ installation of MDPE line pipe alongwith steel pipeline (alongwith installation of required accessories as mentioned above) of following sizes, including executing all works; fabrication, access for construction; supply of all materials (except Owner supplied materials), consumables, labour and other incidental works and handing over the same after return of the surplus pipes to the Owner's designated stockyard(s); carrying out all temporary, ancillary, auxiliary works required to make the MDPE pipeline ready for commissioning as per drawings, specifications, scope of work indicated in PJS and other provisions of Contract document and instructions of Engineer-in-charge. | Item224 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
225 | UP to Dia 90mm | Item225 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
226 | Dia 125mm | Item226 | 5000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
227 | Note : The quantities indicated above against all individual item are tentative and may vary considerably depending upon site condition, methodology adopted as per site requirement with due approval of Owner/ Consultants. | Item227 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
228 | PIPING WORKS FOR SECTIONALISING VALVE STATION-CUM-TAP-OFF POINT All works for fabriaction and installation of all piping above ground at all elevations and below ground at all depth for Sectionalising Valve Station alongwith preparation of construction drawings duly approved by EIC, in all type of terrains and soils including transportation and handling of all Owner supplied materials i.e. extended stem butt welded sectionalising gas actuated ball valve, other types of valves, line pipes for mainline, 4" NB pipe for all branch line including ventlines from Owner's designated place(s) of issue to work site. | Item228 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
229 | Contractor shall supply all required size & type of piping material like pipes, fittings & flanges etc. as per PMS alongwith 2" NB pipe for all branch line & vent line (wherever required) including supply of all consumables, manpower, machinaries, materials etc. and carrying out all mechanical works of underground and above ground piping including fabrication, welding, nondestructive testing of welds, weld repairs/ retesting, cleaning/ flushing, pre-hydrotesting & hydrostatic testing, dewatering, functional testing, cutting of mainline and bevelling (if required) | Item229 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
230 | assembly, including radiography of tie-in joints, corrosion, coating and external painting as required, installation of instruments like pressure/ temperature instruments/ gauges alongwith complete SS Tubing works including supply of SS Tube and thier accessories etc., as required, obtaining all statutory clearances, approvals and permissions for the works (wherever required), making of valve pit (for detail refer relevant drawings) for SV Stationscum- tap-off points enclosed with tender filled with sand, excavation and filling in all types of soils including soft/ hard rock for installation of piping/ pipe supports providing pipe supports, area fencing and gate including all associated civil and structural works; painting, finishing, clean-up and restoration of site; preparation of as-built drawings, documents and project records and performing all works as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge. In this item, instead of Brick Work RCC will be done | Item230 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
231 | Type - I SV Station on 10" Pipeline | Item231 | 1 | Lumpsum for each |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
232 | Note: i) Work under above items are exclusive of all works associated with main pipeline covered under Item No. 1.0 above. ii) All civil/ structural works including area fencing and gate, valve pits except for piping support will be paid separately as per unit rate provided elsewhere in the SOR. iii) All coupling, nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under above item rate. | Item232 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
Total in Figures | [51 empty] | 0 | 0 | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## BoQ3 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR | [49 empty] | 1
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Maharastra Natural Gas Ltd.,Pune
Name of Work: TENDER FOR LAYING & CONSTRUCTION OF 12” NB X 3 KM , 6" NB X 0.2 KM & 4" NB X 1.5 KM U/G STEEL PIPELINE NETWORK & ASSOCIATED WORKS FROM MNGL CGS NEAR VEDIKA LAWNS, MEHKAR TO HOTEL MOGRA, MEHKAR & SURROUNDING AREAS IN NANDED GA (Section No-03)
Tender No: MNGL/CP/2024-25/109
Do you want to quote for this sheet ? |  |  | Yes
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE / SCHEDULE OF RATES (SOR) (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Rate inclusive of all taxes and duties except Goods & Service Tax (Rs.) | Per Unit Goods & Service Tax (GST) In % (To be entered by the Bidder) | GST in Rs. | Unit rate inclusive of all taxes & duties including GST (Rs.) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | CARBON STEEL PIPES | Item1
2 | PIPELINE LAYING / INSTALLATION in all type of surface (Normal/built-up surface) "Receiving and taking over" as defined in the specifications, handing, loading, transportation and unloading of Owner supplied 3-Layer PE coated linepipes from Owner's designated stack-yard to Contractor's stock yard/workshop/work-site including preliminary activities, preparation of drawings, wherever required for crossing etc. including handling, stacking, stringing on the pipeline Right-of-Use/ pipeline route alignment, carrying out inspection of company supplied materials including linepipes at the time of taking over, laying/ installation of coated linepipes, associated burried valves, barred tees, insulating joints, flanges & fittings of all sizes, thickness & ANSI class rating and accessories as per specification wherever required depending on site condition including execution of all works, "taking over", handling , including loading and unloading, transportation of Owner supplied materials other than linepipe from Owner's designated place (s) of issue to work site, | Item2
3 | additional lands required for Contractor's storage, fabrication, access for construction, procurement and supply of all materials (except Owner supplied materials), consumables, equipment, labour and other inputs, carrying out all temporary, ancillary, auxiliary works, aquistion of ROU/ROW for laying of pipeline from HDD Exit and entry point to Tie in Point of existing Pipeline/ ROU, ready for commissioning of pipeline as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge, including but not limited to carrying out the following works: | Item3
4 | Surveying of route and detours required at the time of execution including marking the same in topographical sheet, preparation of construction drawings showing survey details, and submit same to Owner for review / approval. | Item4
5 | Staking and installation of construction markers, clearing, fencing, grubbing, cutting of trees, full filling all the requirements of various statutory/ environment authorities to the entire satisfaction of concerned authorities, grading of work area. Shifting of all obstruction within the ROU/ Pipeline route alignment viz. electrical lines/ poles, telephone line / poles, etc. coordination with concerned authorities and obtain permissions from these authorities. | Item5
6 | Trenching to all depths by excavation in all types of soils including soft/ hard rock and different type of pavement / footpath / roads etc. including rock breaking, chiselling or otherwise cutting etc. as required and storing excavated soil, reusable materials at designated area as directed by Engineer in charge and to a width to accommodate the Steel pipeline and MDPE as per the relevant standard/ specification etc. [The minimum depth of the top of pipeline shall be 1.2m measured from top of pipeline coating to the top of undisturbed surface of the soil or as per SCC/ OISD - 141 / 226, whichever is higher]. Dewater of trenches if required as per site condition. | Item6
7 | Carrying out repairs of pipe defects/ replacement in case of irreparable defects and repairs of defects of pipe coating not attributable to Owner including defects/ damages occurring during transportation / handling. | Item7
8 | Stringing of line pipes along pipeline trench / ROU on straw / sand / soft soil bags including supply of bags and its filling materials. | Item8
9 | Checking, cleaning, aligning, bending, cutting and bevelling (as required) of pipes for welding and field adjustments including pipe fittings, welding, carrying out non-destructive testing of welds as required including 100% radiography by X-ray and providing all requisite equipment, labour, supervision, materials, films, consumables, all facilities and personnel to process, develop, examine and interpret radiographs and other tests as required, carrying out repairs of weld joints found defective by Engineer-in-Charge, carrying out re-radiography and other tests as required on repaired joints. | Item9
10 | Carrying out installation of carrier line pipe at all minor crossing viz. carttrack, pathway, water bodies etc. at designated depth by open cut (except at crossing by HDD method). | Item10
11 | Carrying out installation of carrier line pipe in the casing pipe at cased crossing (excluding installation of casing pipes which is covered separately). | Item11
12 | Coating of field weld joints, long radius bends (R=3D), elbows, buried fittings and valves etc. including supply of coating materials etc. (i.e. heat shrinkable sleeves and high build epoxy etc.) as per PJS & Technical Specification compatible with 3 layer PE coating material of the line pipe. | Item12
13 | Counting the number and type of trees cut in presence of DFO/concerned authorities and keeping record thereof, stacking and handing over of all cut tress. | Item13
14 | Installation / lowering the pipeline in trench to required depth as per PJS, Techanical Specification & drawings, supply & placement of 1.0mm thk. HDPE Yellow colour warning mat,RCC tiles (300 mm width x 50 mm thick) over the pipeline & MDPE Pipe in same trench along the complete route as per standard drawings, data sheets & technical specifications, padding around pipeline as per Standard Drg. no. MNGL/Plng./Steel/03 with suitable soil duly approved by EIC including supply of padding material, backfilling and its compaction to the satisfaction of concerned authorities with excavated earth / borrowed select soil including supply of borrowed select soil duly approved by EIC before backfilling and make ready for restoration to be done by Onwer / concerned authorities. | Item14
15 | Supply and installation of slope breakers, wherever required or, as directed by Onwer / Engineer–in–charge. | Item15
16 | Crossing the all-foreign pipeline / HT line / cable / any other utilities etc. with necessary concrete / HDPE sheet protection including coordination with all agencies and obtaining NOC | Item16
17 | Supply and installation of bank protection alongwith backfill materials duly approved by EIC for pipeline trench and banks falls under minor water body crossing as per technical specification & Std. Drg. No. MNGL/Plng./Steel/28, wherever required or, as directed by Onwer / EIC. | Item17
18 | Training and diversions of streams in steep slope area, wherever required. | Item18
19 | Carrying out air cleaning, pigging, flushing, cleaning and hydrostatic testing of complete pipeline with required quantity of corrosion inhibitor including pre-testing of designated sections complete as per specification and approved by Engineer–in–charge to specified pressures indicated elsewhere and duration after stabilization as per specification, providing all equipment, pumps, fittings, instruments, dead weight tester, pressure recorder, thermocouples etc., and services, supervision, labour, consumables, water including supply of corrosion inhibitor, air, etc. as required, locating of leaks and rectification of defect attributable to Contractor (rectification of defects in linepipe material not attributable to contractor shall be paid separately as per other item of schedule of rate), re-testing after rectification, dewatering after successful completion of hydrotesting of entire section and as per specification | Item19
20 | All tieing-in, including the tie-in(s) of the pipeline with the adjacent sections of pipeline including cutting of test header, rebevelling as required, radiography and other NDT examination, joint coating as per specification. | Item20
21 | Final clean-up of right-of-use or area disturbed by contractor during their construction activities for laying of pipeline works and disposal of debris and surplus material to designated disposal areas and backfilling of trench and compaction of the same as per satisfaction of Owner and / Or as directed by Engineer–in–charge. | Item21
22 | Installation of all burried valves (except extended stem valves) inside the valve pit and making provision to operate the valve. | Item22
23 | Preparation of as-built drawings, pipe-books (1 set of tracing on polyester film and 6 sets of as-built drawings and 1 soft copy and 6 hard copies of pipe book) All the works shall be executed in accordance with the provision of contract including carrying out all temporary/ ancillary/ auxiliary works required for the performance of the works and all other acts, deeds, matters and things necessary to make the pipeline ready for precommissioning activities. | Item23
24 | Raking up of hard surface of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. Payment for cutting of hard rock, if any, is covered unders SOR no. 96 | Item24
25 | Specified dia Thk (mm) Material Coating Type Length of each pipe (mm) NB | Item25
26 | 305 (approx.) 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item26 | 3000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
27 | 150 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item27 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
28 | 100 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item28 | 1170 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
29 | Note: This item shall be applicable for the underground steel grid main pipeline & branch pipeline, barred tees, insulating joints, bends, flanges & fittings, accessories etc. (i.e. including arrangement for making provision for tap-off on proposed steel grid main pipeline) and aboveground approach pipeline upto Insulating Joint (excluding installation of aboveground insulating joint) for various stations. | Item29
30 | Items except above are covered separately. The lengths of pipelines are tentative. | Item30
31 | Permission Liasioning /Follow-up | Item31
32 | Liasioning & follow up for Permission with all the concerned authorities & boards viz Railways, NH, PWD, MIDC, Local Municipal, Panchyat, Electricity, REC, RES, Sewage water, Drinking water, Forest, Social Forestry, Owners of OFC, Traffic, Law & Order, Fire Brigade, Private Land Owner etc. for entire pipeline length and associated terminals (like SVs, tap-offs) alongwith associated work as per tender. | Item32 | 4700 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
33 | Laying of RCC Tiles | Item33
34 | Providing single layer of RCC Tiles with supply of RCC Tiles to entire width of trench above Warning Mat placed in trench over the laid pipeline as per standard drawing, specification and instruction of Owner. (Rate to include cost of all labour, tools, tackles, equipment, hire charges & supply of all materials, etc.) | Item34
35 | For width of 12" pipeline trench | Item35 | 3000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
36 | For width of 6" pipeline trench | Item36 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
37 | For width of 4" pipeline trench | Item37 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
38 | Barricading to comply with HSSE | Item38
39 | Steel barricading of the trenches Cautionary Sign Boards and lighting arrangement shall be provided as per attched drawing no.MNGL/Plng./steel/04. The rates include barricading of trenches along with sign boards, lighting etc. and maintain the same till the back filling of the trench. Rates will be payable per metre of BARRICADING PROVIDED. If proper barricading is not provided, MNGL will barricade the trenches at the risks and costs of the CONTRACTOR and will levy penalty of twice the rate per unit for the relevant section of the pipeline apart from other actions as per contract. | Item39 | 4700 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
40 | RESTORATION OF ROADS Restoration of asphalt / concrete / red stone roads / pavement/Footpath/Paver block including compaction of soil, to original condition as per requirement and to the entire satisfaction of EIC and / or concerned Owners having jurisdiction for following thickness. | Item40
41 | Restoration of Asphalt road upto 10 cm thickness | Item41 | 600 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
42 | Restoration of Asphalt road beyond 10 cm upto 20 cm thickness | Item42 | 100 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
43 | Restoration of Concrete road upto 10 cm thickness | Item43 | 300 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
44 | Restoration of red stone road / footpath / pavement/ Paverblock upto 4 cm thickness | Item44 | 300 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
45 | BORROWED SELECT SOIL FOR BACKFILLING Additional work over and above item 1.0 for supply of specified and approved quality of borrowed soft graded soil / sand in place of available excavated material and / or other suitable soil as per applicable standards / specifications, including backfilling of excavated trench for specified length after laying and padding of pipeline, including transportation of such special backfill material over all distances, complete. | Item45 | 750 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
46 | CROSSING OF STEEL PIPELINE BY OPEN CUT | Item46
47 | Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insatllation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed. | Item47
48 | Road Crossing By Open Cut Method Road Crossings at various locations by Open cut Method along with laying of MDPE upto 180 mm Dia if necessary as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item48
49 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item49 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
50 | Line pipe detail 6" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item50 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
51 | Line pipe detail 4" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item51 | 60 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
52 | Water body Crossing By Open Cut Method water/ canal/ nallah/ drain/ channel Crossings at various locations by Open cut Method along with laying of MDPE upto 180 mm Dia if necessary as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item52
53 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item53 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
54 | Line pipe detail 6" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item54 | 10 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
55 | Line pipe detail 4" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item55 | 40 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
56 | Note: Laying of the pipeline by the approved method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item56
57 | Backfilling of the Road/water/ canal/ nallah/ drain/ channel Crossings/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority. | Item57
58 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item58
59 | CROSSINGS/LAYING ALONG THE ROAD BY HDD METHOD | Item59
60 | Complete work of the any crossing (between the limits are defined as approved drawings) by HDD method including "Receiving and taking over" owner supplied three layer PE coated line pipes from Owner's designated place to issue/ dump site(s) and transportation to Contractor's stock yard/ work shop/ work site including all handling loading, unloading, aligning etc. supply of all Contractor supplied material, manpower, equipment, other resources and aquiring the required land for storage, fabrication inclduing string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type Heat Shrink Sleeve and repair of pipeline coating with special repair patch materials as per specification,pre-testing etc. of complete string made for crossing access for Contractor etc and execution of, but not limited to, following works in accordance with specifications scope of work and instructions of Engineer-in-charge and as per all provision of Contract Document. | Item60
61 | Pre-construction surveys based on site visit, collection of historical data from irrigation/ concerned department including design & calculation and detail engineering and making of crossing drawing for getting their approval from concerned Authority/ Engineer-in-charge, getting work permit/ NOC for water crossings/ road crossings as well as utility crossings (if any) encountered during crossing prior to start the execution of work. | Item61
62 | Directional drilling to required depth from top of road including maintenance of drill hole in all types of strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) at all depth to accommodate the pipeline at all conditions encountered during rail/ road crossing by approved HDD methods for providing minimum cover specified in code/ specification or the actual depth as decided by concerned authority, whichever is more. | Item62
63 | In case of water crossing, drilling to the required depth on the banks and bed including maintenance of drill hole in all types of soil strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) all depth to accommodate the pipeline a by HDD methods for providing with minimum cover over top of the pipe at all point across the maximum possible width of water bed (as per drawing) either 1.5 mtrs. below the predicted scour profile expected during the life time of the pipeline or 2.5 mtrs. below the available lowest firm bed (if scour profile/ depth not available) of the water crossing by ascertaining bed level upto 50 mtrs. both the side from crossing location or the actual depth as decided by concerned Authority/ Engineer-in-charge whichever is more. | Item63
64 | Laying of the pipeline by the approved HDD method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints with special type Dirax Heat Shrink Sleeve or equivalent and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item64
65 | Backfilling of the ditch/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority and all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specification, approved drawings, calculations, methods and to the satisfaction of Engineer-in-charge and/or as directed by concerned Authority. | Item65
66 | Post installation hydrotest dewatering and tie-in with pipeline at either side of crossing/banks etc. | Item66
67 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item67
68 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 (along with laying of 4'' Steel Pipe for MDPE if necessary) by HDD Method . | Item68 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
69 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 150 mm NB x 6.4 mm thk. of API X-52 (along with laying of 4" Steel Pipe for MDPE if necessary) by HDD Method. | Item69 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
70 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 100 mm NB x 6.4 mm thk. of API X-52 (along with laying of 4" Steel Pipe for MDPE if necessary) by HDD Method. | Item70 | 60 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
71 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item71 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
72 | Laying along the Road by carrier pipeline of size 150 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item72 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
73 | Laying along the Road by carrier pipeline of size 100 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item73 | 50 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
74 | Installation of carrier pipes by rock drilling for Road/water/Canal/ nallah/ drain/ channel/along the road, or wherever required in all types of hard rock. It includes survey of the underground utilities, submission of profile for approval, execution of the work as per the standard procedure, including , excavation of the pits, insertion/pulling of the carrier pipe, removal of malba, subsequent backfilling and restoration of the facility crossed as per original condition, including supply of all other materials, equipment, consumables, manpower etc including string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type of Heat Shrink Sleeve (Direx) and repair of pipeline coating with special repair patch materials as per Specification, pre-testing etc. of complete string made for crossing/ laying access for Contractor etc. and execution of, but not limited to, following works in accordance with specifications and instruction of Engineer-in-Charge and as per all provision of Contract Document. Balance activities as defined in SOR Item of open trench. Note:The length of HDD mentioned is tentative and may vary to the considerable extent depending upon requirements as per site conditions. The length mentioned in SOR is indicative for all the crossing to be done by HDD, numbers and locations shall be decided by Engineer-in-Charge depending upon site condition. Payment for the length of final tie-in carrier pipeline string with mainline laid by HDD are inclusive in this above item rate. No separate payment shall be made under other clauses mentioned elsewhere. Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item74
75 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 (along with laying of 4'' Steel Pipe for MDPE if necessary) by HDD Method . | Item75 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
76 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 150 mm NB x 6.4 mm thk. of API X-52 (along with laying of 4" Steel Pipe for MDPE if necessary) by HDD Method. | Item76 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
77 | Crossing of nallah/ drain/ channel /River crossings by carrier pipeline of size 100 mm NB x 6.4 mm thk. of API X-52 (along with laying of 4" Steel Pipe for MDPE if necessary) by HDD Method. | Item77 | 60 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
78 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item78 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
79 | Laying along the Road by carrier pipeline of size 150 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item79 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
80 | Laying along the Road by carrier pipeline of size 100 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item80 | 60 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
81 | Note: (i) Crossing width & Actual string length for HDD shall vary as per design calculations & site condition so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. | Item81
82 | (ii)Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item82
83 | (iii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by HDD method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item83
84 | (iv) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossing at different locations. | Item84
85 | (v) The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. | Item85
86 | Note: (i) Quantity mentioned under item nos. 48 , 52 are indicative only for different location of roads/water/ canal/ nallah/ drain/ channel Crossings. (ii) Actual length & width of individual crossing and cover from top of casing pipe/ carrier pipe string may vary depending upon site condition, approved crossing drawings, specifications etc. and / or as decided by Engineer-in-charge/ Concerned Authority. | Item86
87 | (iii) Payment for supply & installation of Zinc ribbon anode and its design excluded from above item and covered elsewhere in the SOR. (iv) Payment for the length carrier pipeline string inserted in casing pipe laid by Boring are covered separately and shall be paid under other clauses mentioned elesewhere in the SOR. | Item87
88 | Excavation beyond 1.5m depth in case of crossing of utilities/ drain/ culverts etc. through open cut upto the following depth (including restoration of the damaged area to its original condition and satisfaction of the Engineer-in-charge / concerned authorities) : - | Item88
89 | In all type of surface (Kachha/ built-up surface / Hard surface) of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. The other activities are as per SOR 1.1. Payment for cutting of hard rock, if any, is covered unders SOR no. 96 | Item89
90 | Deeper than 1.5 m & upto 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item90 | 500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
91 | Deeper than 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item91 | 300 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
92 | Deeper than 1.5 m & upto 2.5 m below existing level (for 150 (approx.) mm NB Pipeline) | Item92 | 40 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
93 | Deeper than 2.5 m below existing level (for 150 (approx.) mm NB Pipeline) | Item93 | 40 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
94 | Deeper than 1.5 m & upto 2.5 m below existing level (for 100 (approx.) mm NB Pipeline) | Item94 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
95 | Deeper than 2.5 m below existing level (for 100 (approx.) mm NB Pipeline) | Item95 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
96 | Excavation of hard rock | Item96
97 | Excavation of hard rock wherever hard rock of single piece exceeding 1.0 m in length removable by pneumatic chisel/ drill as per direction of EIC. | Item97 | 3000 | Cub. M |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
98 | REPAIR OF COATING DEFECTS (NOT ATTRIBUTED TO CONTRACTOR) | Item98
99 | Repair of Holiday in Coating (Noted and recorded at the time of "receiving and taking over") Supply of all coating repair materials as per requirements of specification to be compatible with line pipe coating material, supply of all consumables, utilities, equipments and all manpower required, pipe cleaning and surface preparation, repairing of coating defects (resulting in holiday) and testing including all handling, transportation, etc. for line pipes, performing all works necessary for the completion of the works stirctly in accordance with relevant specification and instructions of Engineer-In-Charge. This rate shall be applicable per sq. cm of the exposed steel area exposed steel area. | Item99 | 2000 | Sq. cm. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
100 | PERMANENT MARKERS Supply, fabrication and installation of all types of permanent markers along the route including all associated civil works such as excavation in all types of soil, construction in all types of soil, construction of pedestals and grouting with concrete, clearing, supply and application of approved colour and quality of primer and paint, stencil letter cutting for numbers, direction, change etc., restoration of area to original condition and performing all works as per drawing, specification and instruction of engineer-in-charge. | Item100
101 | Pipeline RCC boundary / route marker as per drawing | Item101 | 60 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
102 | Pipeline warning markers with post & foundations | Item102 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
103 | Pipeline direction marker with post & foundations | Item103 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
104 | Pipeline KM with post & foundations | Item104 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
105 | HOOK -UP | Item105
106 | Hook-up of proposed pipeline by welding of final tie-in-joint with any existing laid pipeline portion of river X-ing ,existing Tap-off & battery limit of section IV including Hook-up point of the existing pipeline to be made ready for welding by cutting of flanges / valves / headers at all depth in all type of soil etc. Venting of N2 / gas / gas mixture as required purging of N2 Gas (if required), rebevelling as required, radiography and other NDT examination, joint coating as per specification.Contractor shall supply of all consumables, manpower, machinaries, materials, N2 gas etc. and carry out all works as per the provisions of Contract document and instructions of Engineer-in-charge. | Item106
107 | For 12" NB | Item107 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
108 | For 6" NB | Item108 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
109 | For 4" NB | Item109 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
110 | PRE-COMMISSIONING AND ASSISTANCE IN COMMISSIONING OF PIPELINE SYSTEM Swabbing, drying, purging with nitrogen of the complete pipeline network and the associated facilities being installed to the specified acceptance criteria, carrying out pre-commissioning works, providing assistance during the complete duration of commissioning operations for entire pipeline network system including supply of all equipment, man-power, consumables (including pigs & nitrogen required for purging with maintaining nitrogen column of mininum 10% of pipeline geometric volume) materials for all temporary works and performing all associated works, complete as per the relevant specifications, other provisions of Contract document and instructions of Engineer-in-charge. | Item110
111 | For 12" NB Pipeline | Item111 | 3000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
112 | For 6" NB Pipeline | Item112 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
113 | For 4" NB Pipeline | Item113 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
114 | IDLE TIME PRESERVATION OF PIPELINE Preservation of complete pipeline and associated facilities forming part of the pipeline as per Bid document and its maintenance including supply of all consumables, all equipment, manpower, etc. complete as per the requirements of specifications, other provisions of Contract document and instructions of Engineer-in-charge. Note : Owner reserves the right to exercise either or none of the rates below. | Item114
115 | By filling and pressurizing with nitrogen to a pressure of 2 bar(g) for a period of 3 months. | Item115
116 | For 12" NB Pipeline | Item116 | 3000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
117 | For 6" NB Pipeline | Item117 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
118 | For 4" NB Pipeline | Item118 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
119 | For every additional period of one month or part thereof | Item119
120 | For 12" NB Pipeline | Item120 | 3000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
121 | For 6" NB Pipeline | Item121 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
122 | For 4" NB Pipeline | Item122 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
123 | RCC VALVE PITS All civil works including supply of all materials, excavation of pit, piping supports including all PCC and RCC works for valves pits including pedestals with insert plates as required sealing of pipe at valve pits, providing cover etc. and finishing , clean-up and restoration of site, filling and grading of area around valve station for avoiding any local flooding of area, as per typical drawing and specification enclosed and instructions of Engineer-in-charge. In this item, instead of Brick Work, RCC will be done | Item123
124 | Valve Pit of Size 2m x 2m | Item124 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
125 | Valve Pit of Size 1.5m x 1 m | Item125 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
126 | Valve Pit of Size 1 m x 1 m | Item126 | 5 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
127 | SUPPLY OF ASSORTED PIPE, FITTINGS AND FLANGES Complete works of supply of pipes, flanges & fittings for aboveground & underground installation including all taxes, duties, transportation and inspection charges but not limited to, the following items in accordance with PMS (piping material specification), relevant specifications & drawings indicated in job specification under SCC (technical) and instructions of Engineer-in-charge and as per all provisions of the CONTRACT DOCUMENT. - Handling including lifting, transportation from Contractor Stores to CONTRACTOR's workshop for fabrication and/ or to work site for field fabrication and erection for all piping items supplied by Contractor. | Item127
128 | Carbon Steel Pipe (A 106, Seamless B-36.10/ API X 52 ) | Item128
129 | Size Rating/ Schedule | Item129
130 | 2" NB, BE Sch. 80 | Item130 | 35 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
131 | 1" NB, PE Sch. 80 | Item131 | 18 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
132 | ¾" NB, PE Sch. 160 | Item132 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
133 | Flanges | Item133
134 | Weld Neck (B-16.5, 300# A105,125 AARH, Serrated finish) | Item134
135 | Size Rating/ Schedule | Item135
136 | 6" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item136 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
137 | 4" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item137 | 5 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
138 | 2" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item138 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
139 | 3/4" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item139 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
140 | Blind Flanges (B-16.5, 300# A105,125 AARH Serrated) | Item140
141 | Size | Item141
142 | 6" NB, RF | Item142 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
143 | 4" NB, RF | Item143 | 5 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
144 | 2" NB, RF | Item144 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
145 | 3/4" NB, RF | Item145 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
146 | Elbow (Seamless) | Item146
147 | 90° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item147
148 | Size Rating/ Schedule | Item148
149 | 12" NB 300# | Item149 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
150 | 6" NB 300# | Item150 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
151 | 4" NB 300# | Item151 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
152 | 2" NB Sch. 80 | Item152 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
153 | 45° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item153
154 | Size Rating/ Schedule | Item154
155 | 12" NB 300# | Item155 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
156 | 6" NB 300# | Item156 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
157 | 4" NB 300# | Item157 | 10 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
158 | 2" NB Sch. 80 | Item158 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
159 | 90° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item159
160 | Size Rating/ Schedule | Item160
161 | 12" NB 300# | Item161 | 16 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
162 | 6" NB 300# | Item162 | 5 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
163 | 4" NB 300# | Item163 | 14 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
164 | 45° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item164
165 | Size Rating/ Schedule | Item165
166 | 12" NB 300# | Item166 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
167 | 6" NB 300# | Item167 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
168 | 4" NB 300# | Item168 | 10 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
169 | 22½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D) Min Thickness 6.4mm | Item169
170 | Size Rating/ Schedule | Item170
171 | 12" NB Sch. Std. | Item171 | 14 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
172 | 6" NB End thickness to match with pipe wall thickness | Item172 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
173 | 11½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D), Min Thickness 6.4mm | Item173
174 | Size Rating/ Schedule | Item174
175 | 12" NB 300# | Item175 | 14 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
176 | 6" NB 300# | Item176 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
177 | Tees (Seamless) | Item177
178 | Equal Tee (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item178
179 | Size Rating/ Schedule | Item179
180 | 12" NB x 12" NB x 12" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item180 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
181 | 6" NB x 6" NB x 6" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item181 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
182 | 4" NB x 4" NB x 4" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item182 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
183 | 2" NB x 2" NB x 2" NB Sch. XS | Item183 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
184 | Unequal Tee (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item184
185 | Size Rating/ Schedule | Item185
186 | 12" NB x 12" NB x 6" NB Sch. Std. x Sch. Std. | Item186 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
187 | 12" NB x 12" NB x 4" NB Sch. Std. x Sch. Std. | Item187 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
188 | 4" NB x 4" NB x 2" NB Sch. 80 x Sch.80 | Item188 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
189 | 6" NB x 6" NB x 4" NB Sch. Std.x Sch. XS | Item189 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
190 | Reducer (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item190
191 | 12" NB x 6" NB Min Thickness 6.4mm | Item191 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
192 | 12" NB x 4" NB Min Thickness 6.4mm | Item192 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
193 | 6" NB X 4" NB Min Thickness 6.4mm | Item193 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
194 | 4" NB X 2" NB Min Thickness 6.4mm | Item194 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
195 | Weldolet and Sockolet | Item195
196 | Weldolet (MOC A105 & DIM. MSS SP 97) | Item196
197 | Size Rating/ Schedule | Item197
198 | 12" NB x 2" NB Sch. 80. | Item198 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
199 | 6" NB x 2" NB Sch.80 | Item199 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
200 | 4" NB x 2" NB Sch. 80 | Item200 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
201 | Sockolet (MOC A105 & DIM. MSS SP 97) | Item201
202 | 12" NB x 3/4" NB #6000 | Item202 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
203 | 6" NB x 3/4" NB #3000 | Item203 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
204 | 6" NB x 1" NB #3000 | Item204 | 5 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
205 | 4" NB x 3/4" NB #3000 | Item205 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
206 | Butt Weld Disc End Cap (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item206
207 | Size Rating/ Schedule | Item207
208 | 12" Sch. Std. | Item208 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
209 | 6" Sch. 40 | Item209 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
210 | 4" Sch. 80 | Item210 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
211 | Fabrication & Installation of Underground Valve Assembly | Item211
212 | 12"NB Isolation Valve/tap-off assembly as per Drg. No. MNGL/Plng./Steel/40 | Item212 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
213 | 6" NB Isolation Valve/tap-off assembly as per Drg. No.MNGL/Plng./Steel/40 | Item213 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
214 | 4" NB Isolation Valve/tap-off assembly as per Drg. No. MNGL/Plng./Steel/40 | Item214 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
215 | Note: | Item215
216 | For all the supply items mentioned above, procurement shall be made as per enclosed Data Sheets and respective technical specification, after due approval of Engineer-in-charge. | Item216
217 | The quantities mentioned above are tentative and quantities for above supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item217
218 | PLANT PIPING (ABOVEGROUND) Fabrication and testing of carbon steel piping and fittings, valves, IJ, including supply of all consumables, equipment, manpower, and other resources and execution of job as per instruction AIC/EIC.Transportation of all piping items from Owner's and/ or Contractor's storage point to work at site/ workshop as applicable, complete work of fabrication, erection, painting, testing of pipes, flanges and fittings and making ready for further Commissioning / Start-up of carbon steel piping of all sizes and ratings including supply of all consumables, equipment, manpower and other resources and execution of, but not limited to, as per all provisions of the CONTRACT DOCUMENT. | Item218
219 | Fabrication including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site, cutting, edge preparation, inclusive of grinding the edges of pipes, fittings, flanges, reducers etc. to match with the matching edges of uneven thickness, wherever required, fit-up, welding of pipes and fittings like elbows, tees, reducers, weldolets, sockolets, Valves, IJ etc. flanges, vent and drain point connection, Radiography and NDT of all joints etc, including providing stubin connections, fabricated fittings and reinforcement pads etc., as required. | Item219
220 | Erection of pipes of all types and thickness at all elevations, connecting with equipment nozzle, aligning, installation and carrying out connected activities for all types of valves, all online instruments and fittings of all sizes of elbow, reducers, tees, flanges, blind flanges, spectacle blind flanges, branch connection / tapping for pressure gauges, including installation of gaskets and bolts. | Item220
221 | Erection including prior cleaning, lifting, placing on pipe sleepers and supports, overhead on racks, skids and at all elevations including installation and carrying out connected activities for all types of valves including supply and fixing of gaskets, studs/ bolts, nuts wherever required for all sizes, levelling, aligning, joining of flanges, blind flanges, connecting with equipment, nozzles, strainers, tie-in with existing piping/facilities, etc. tapping for inline instruments like pressure gauges, thermowells, sample connection, etc. | Item221
222 | Hydro testing of the piping job shall be conducted at pressure mentioned in specification for a period of 4 hours by using de-mineralised water, to check its strength. No visible leakages shall be detected during the test. Testing shall be conducted as per tender specification. | Item222
223 | Preparation of final bill of material based on piping GADs. | Item223
224 | Preparation of isometric and fabrication drawings. | Item224
225 | Carrying out Non-destructive testing as required except items mentioned in sl. no. 286 of SOR. | Item225
226 | Painting of entire system (including aboveground all pipes fittings, flanges and accessories) as per specifications suitable for highly corrosive area environment including supply of approved paints and primers, application of primer and paints, indentification lettering/ numbering, colour coding, etc. as specified including rub down & touch up of shop primer or scrapping of shop primer wherever required by COMPANY and providing scaffolding for all heights etc. | Item226
227 | Cleaning and flushing by water/ compressed air, testing of the systems including hydrostatic, pneumatic and any other type of testing as specified, draining, drying by compressed air/other methods approved by COMPANY. | Item227
228 | Precommissioning & making operational all piping system and equipments. | Item228
229 | Commissioning Contractor scope shall provide all necessary assistance in term of supply of man-power, equipment, tools and tackles required amount of nitrogen for purging of entire terminal piping system including equipments etc. to the company during commissioning activities. | Item229
230 | Completion of all such work in all respects as per scope of work and as per drawings, specifications and instructions of the COMPANY and keeping the system ready in all respects for further commissioning and start up. | Item230
231 | Hook-up works (with client/ consumer piping at battery limits): | Item231
232 | Complete Carbon Steel aboveground Piping Work with painting including all fittings, flanges and supply of all required gaskets, studs bolts & nuts etc., and Any other work and material required for the completion of the work and not covered above and desired by EIC shall be in the scope of contractor | Item232
233 | Carbon Steel Pipe (ASTM A 106, Seamless B-36.10 / API X 52) | Item233 | 400 | inch Dia |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
234 | 1) Pipe Specification and thickness may vary depending upon availability of pipe. No extra payment shall be made for this. 2) All butt welded fittings & flanges end shall generally match with connecting pipe wall thickness. However, in case of misalignment, Contractor shall have to do end preparation without any extra cost. 3) All o-lets less than 2" NB size, all sizes of coupling and nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under erection rate. | Item234
235 | Aboveground installation of Insulating Joint & Valves etc. Handling including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site and installation of all types of valves, insulating joint including assembly of valve accessories, (if any) by bolting, threading or welding, supply and insertion of gaskets, nuts & bolts, nipples, etc. at all elevations of pipe sleepers, supports or overhead on racks, equipments nozzle, skid & painting etc. supply of all consumables, manpower, equipment, etc. for completion of all works as per scope of work and as per drawings, specifications and instructions of Engineer-in-charge including servicing/ cleaning of valve wherever requried. | Item235
236 | Welded Valves (Full Bore/ Reduced Bore) Ball / Globe / Check Valve | Item236
237 | Size Rating/ Schedule | Item237
238 | 4" NB 300# | Item238 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
239 | 2" NB 300# | Item239 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
240 | Sockolet Welded Valve (Ball / Globe Valve) | Item240
241 | Size Rating/ Schedule | Item241
242 | 1" NB 800# | Item242 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
243 | ¾" NB 800# | Item243 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
244 | 12" NB, 300# - Insulating Joints | Item244 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
245 | 6" NB, 300# - Insulating Joints | Item245 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
246 | 4" NB, 300# - Insulating Joints | Item246 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
247 | STRUCTURAL WORKS | Item247
248 | Supply of erection of single leaf mild steel gate 2.5m high with mesh upto 2m height and barbed wire fencing and 2m wide complete in all respect including painting as per TS on all MS items, all works as per specification and drawings excluding foundations and RCC beams. | Item248 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
249 | Supply of all materials, fabrication and erection of chain link fencing 2.5m high with mesh up to 2m height and barbed wire fenching complete in all respects including painting as per TS on all MS items, all works as per specification and drawings excluding foundation and RCC beams. | Item249 | 150 | RM |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
250 | Pipe Supports & Other Structures | Item250
251 | Supply, fabrication and erection of all types of pipe supports like clamps, saddle, guide stops, cradles, turn buckles, anchors, T-posts; stockade/ trestle and pipe bridge for overhead piping; frames for canopy, approach ladders and platforms, crossover, cable tray supports, etc. including painting suitable for highly corrosive area as per specification labour and supervision & complete work as per drawings, specifications and instruction of Engineerqw-incharge. (Bolts, nuts, washers, U-clamps etc. for supporting shall be supplied by the Contractor within the rates quoted. These items will not be measured and paid seperately). The work is to be completed in all respect as per scope of work and specification. | Item251 | 300 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
252 | Notes: | Item252
253 | The quantities indicated are estimated values and hence are approximate. Final payment will be made based on actual quantities to be certified by the Purchaser. | Item253
254 | The cost of MS bolts (permanent and service(, washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants etc., as required for the work shall be deemed to be included in the quoted rates. | Item254
255 | All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accrodance with time schedule, are deemed be included in the quoted rates. | Item255
256 | CIVIL WORKS | Item256
257 | Site Grading Excavation in earth and filling to the grades and levels shown in the approved drawings in all kinds of conditions including for Road embarkments, using approved quality good earth from designated borrow area, for all heights and depths including clearing and stripping (min. 150mm) of the area marked for filling, taking spot levels, consolidating the exposed natural soil surface, excavating the earth from borrow area loading, transporting & unloading, spreading in layers not exceeding 150mm thickness, breaking clods, watering (if reqd.), ramming and compacting by manual/ mechanical means to give minimum 92% of modified Proctor's density of earth, testing & dressing including disposal of all unserviceable material all complete as per specifications and directions of Engineer-in-charge. | Item257 | 150 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
258 | (Rate to include cost of all labour, tools, tackles, equipment, hire charges, cost of borrow earth by way of royalties, right of way, cess etc., as applicable with all bye works and sundry works). | Item258
259 | Plain Cement Concrete Supplying and laying plain cement concrete (including shuttering of required) in all types of concrete works including levelling courses below foundation, substructure, superstrcuture, chambers, cable tranch, under floors and any other locations, at all leveies as per drawings, specifications and directions of the Engineer-in-charge. | Item259
260 | PCC 1:2:4 1 Cement : 2 Coarse sand : 4 stone aggregate 20mm nominal size. | Item260 | 400 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
261 | Reinforced Cement Concrete Providing and laying reinforced cement of grade M-20 with 20mm and down grade crushed stone aggregate in all types of structures like foundations, pedestals, pedestal bases, pipe supports, sleepers cable trench inlcuding constrcution joints, bitumen painting on surface in contact with soil, providing and fixing reinforcing steel, shuttering, inserts, finishes etc. at all depths and heights complete as per drawings, specifications and direction of the Engineer-incharge. | Item261 | 300 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
262 | Rate to include cost of all labour, tools, tackles, equipment, hire charges, supply of all maerials such as minimum 43 grade cement including sulphate resistant cement for substructures, R/F steel, Inserts, bolts, conduits, bitumen, other minor constrcution materials, shuttering, stanging, earthwork in excavation and backfilling using serviceable earth in all conditions, shorting bailing and pumping out water, testing of concrete, curing etc. with all bye works and syndry works. | Item262
263 | TEMPORARY CATHODIC PROTECTION SYSTEM | Item263
264 | Design, detailed engineering, supply, installation, testing and commissioning of the temporary Cathodic protection system using Mg/ Zn galvanic anodes to protect the external surface of 3 LPE coated entire 5.5 km (approx.) long steel pipeline network against corrosion for design life of minimum 1 year or till commissioning of PCP system whichever is later as per standard specification No. MNGL/Steel/TS/15 for temporary cathodic protection system. Scope shall also include but not limited to the following for completion of jobs: | Item264
265 | Measurement of soil resistivity along the right of way of the main pipeline route as per specification for design & installation of anodes. | Item265
266 | Collection of additional data related to cathodic protection along the right of way of pipeline as per specifications. | Item266
267 | Supply, installation, testing & commissioning of one set of spark gap arrestor with 2 plate Zinc grounding cell of 20 kg net weight each across each insulating joint as per specification. | Item267
268 | Supply, installation, testing & commissioning one set of polarisation cell with zinc anode at all high tension (66KV or higher) electrical power transmission line/Equipment crossing or running parallel to the pipeline for grounding purpose as per specification. The rating shall depend upon anticipated fault current & ground bed resistance at the location of installation. However, the rating of polarisation cell (krick) shall not be less than 5 KA & number of 20 kg net weight zinc anode shall not be less than two. | Item268
269 | Supply & installation of Zinc Ribbon Anodes at 4-8 O’Clock position in the interval of 2 metre (max.) on carrier pipes at all cased crossings i.e. railways/ roads etc. | Item269
270 | Monitoring of the protection system for 6 months. | Item270
271 | All civil/ structural works related to TCP system including supply of bricks, cement & steel etc. required for completion of the system. | Item271
272 | For 12" | Item272 | 3000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
273 | For 6" | Item273 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
274 | For 4" | Item274 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
275 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item275
276 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item276
277 | FIELD INSTRUMENTATION | Item277
278 | PRESSURE INSTRUMENTS | Item278
279 | Supply , Installation of Pressure Gagues and their accessories inclusive of supply of necessary piping materials and tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/ manifolds & hydraulic testing (exclusive of calibration of instruments) as per installation standard attached elsewhere in Tender Document and Supply as per Data Sheet No.MEC/23K8/05/E5/I/001/DS-PG. Give breakup of supply and Installation rate. | Item279 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
280 | CALIBRATION | Item280
281 | Calibration of the instruments listed below including removal of instruments from pre-installed locations like panels, enclosure racks, fields etc. and refixing them back in respective/ required places, providing equipments, necessary test jigs, instrument air and all consumables. Calibration reports shall be prepared and to be submitted to the Purchaser/ Consultant. | Item281
282 | Pressure Gauges | Item282 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
283 | Note: | Item283
284 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item284
285 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item285
286 | Laying of MDPE pipe along with Steel pipe line Excluding supply of all MDPE pipe (PE 80/100,SDR11), but Including supply of Bends, Couplers, End caps, Tees, PE Reducer, CS to PE Fitting, Saddle Tapping, Warming mat, etc. as required to complete the job. ( Particular job specification.) "Receiving and taking-over" as defined in the specification, handling, loading, transportation and unloading of Owner supplied MDPE line pipes (PE80/100, SDR11) of all sizes (as free issue items) from Owner's designated place(s) of issue to Contractor's own stock-yard(s)/ Work Shop(s)/ work-site(s) including proper storing, stacking, identification, providing security & insurance cover , including supply of accessories of all sizes & thickness like Bends, Couplers, End caps, Tee, PE Reducer, CS to PE Fittings, Saddle Tapping, Warning Mat, etc.. | Item286
287 | Stringing/ uncoiling of the MDPE line pipe on the pipeline Right-of-Use, laying/ installation of MDPE line pipe alongwith steel pipeline (alongwith installation of required accessories as mentioned above) of following sizes, including executing all works; fabrication, access for construction; supply of all materials (except Owner supplied materials), consumables, labour and other incidental works and handing over the same after return of the surplus pipes to the Owner's designated stockyard(s); carrying out all temporary, ancillary, auxiliary works required to make the MDPE pipeline ready for commissioning as per drawings, specifications, scope of work indicated in PJS and other provisions of Contract document and instructions of Engineer-in-charge. | Item287
288 | UP to Dia 90mm | Item288 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
289 | Dia 125mm | Item289 | 3000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
290 | Note : The quantities indicated above against all individual item are tentative and may vary considerably depending upon site condition, methodology adopted as per site requirement with due approval of Owner/ Consultants. | Item290
291 | PIPING WORKS FOR SECTIONALISING VALVE STATION-CUM-TAP-OFF POINT All works for fabriaction and installation of all piping above ground at all elevations and below ground at all depth for Sectionalising Valve Station alongwith preparation of construction drawings duly approved by EIC, in all type of terrains and soils including transportation and handling of all Owner supplied materials i.e. extended stem butt welded sectionalising gas actuated ball valve, other types of valves, line pipes for mainline, 4" NB pipe for all branch line including ventlines from Owner's designated place(s) of issue to work site. | Item291
292 | Contractor shall supply all required size & type of piping material like pipes, fittings & flanges etc. as per PMS alongwith 2" NB pipe for all branch line & vent line (wherever required) including supply of all consumables, manpower, machinaries, materials etc. and carrying out all mechanical works of underground and above ground piping including fabrication, welding, nondestructive testing of welds, weld repairs/ retesting, cleaning/ flushing, pre-hydrotesting & hydrostatic testing, dewatering, functional testing, cutting of mainline and bevelling (if required) | Item292
293 | assembly, including radiography of tie-in joints, corrosion, coating and external painting as required, installation of instruments like pressure/ temperature instruments/ gauges alongwith complete SS Tubing works including supply of SS Tube and thier accessories etc., as required, obtaining all statutory clearances, approvals and permissions for the works (wherever required), making of valve pit (for detail refer relevant drawings) for SV Stationscum- tap-off points enclosed with tender filled with sand, excavation and filling in all types of soils including soft/ hard rock for installation of piping/ pipe supports providing pipe supports, area fencing and gate including all associated civil and structural works; painting, finishing, clean-up and restoration of site; preparation of as-built drawings, documents and project records and performing all works as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge. In this item, instead of Brick Work RCC will be done | Item293
294 | Type - I SV Station on 12" Pipeline | Item294 | 1 | Lumpsum for each |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
295 | Note: i) Work under above items are exclusive of all works associated with main pipeline covered under Item No. 1.0 above. ii) All civil/ structural works including area fencing and gate, valve pits except for piping support will be paid separately as per unit rate provided elsewhere in the SOR. iii) All coupling, nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under above item rate. | Item295
296 | Details of Major Road Crossing (Canal/SH/DR/NHAI): Supply, Installation & Insertion of pipeline across Canal / State Highways as per SCC and technical specifications | Item296
297 | Supply & Installation of 24" NB x 6.4mm Wall thk. Casing pipe for Line Pipe 12"NB(6.4 mm thk API 5L Gr X52) & 4" NB, 6.4 mm thk API 5L Gr. X52 pipe by Jacking Boring . Including Insertion of 12" dia and 4" dia (for 125 mm dia MDPE Connectivity) Carrier pipeline in 24" dia casing pipe and connectivity with existing pipeline at both end of National Highways/State Highways/ Railway as per SCC and technical specifications -Supply of Casing Pipe Supply of following casing pipe including handling, loading, transportation & unloading etc. to contractor's own stock yard / worksite(s). -After Completion of insertion of carrier pipe with Connectivity at both end including all works as per the scope of work -Post Hydro testing & Commissioning , Submission of as-built drawing, Submission of Documents - The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. - Rate Should include supply & installation of 250mm Casing pipe for 4" Steel Pipeline for MDPE (if required by Authority & as per the instructions of EIC) | Item297
298 | Note: (i) Crossing width may vary as per site condition. Tenderer are advised to visit site for actual assessment of extent of crossing. Actual length of Boring shall be as per design calculations so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. (ii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by Boring method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item298
299 | (iii) The Contractor has to quote alongwith 4" NB (for 125mm MDPE). No any extra payment shall be made against this item. (iv) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossings at different locations. | Item299
300 | (v) Actual length & cover from top of casing pipe string may vary depending upon site conditions, approved drawings, specification etc. and / or as decided by concerned Authority / Engineer-in-charge. (vi) No Extra Payment for supply & installation of Zinc ribbon to be provided to Carrier pipe & Zinc Anode is to be provided to Casing pipe and its design included in above item | Item300
301 | Supply and installation of 24'' casing pipe,Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insertion of carrier pipe in casing pipe after above ground pretesting at specified test pressure and installation of casing insulators & Zinc ribbon anode as per specification/ drawings. Installation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed (Any type of soil) | Item301 | 60 | Mtrs |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
Total in Figures | [51 empty] | 0 | 0 | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## BoQ4 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR | [49 empty] | 1
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Maharastra Natural Gas Ltd.,Pune
Name of Work: LAYING & CONSTRUCTION OF 12” NB X 6 KM , 6" NB X 0.2 KM & 4" NB X 1.5 KM U/G STEEL PIPELINE NETWORK & ASSOCIATED WORKS FROM HDFC BANK, LONAR TO MAULI AUTO PARTS SHOP NEAR TITVI BRIDGE, PANGRADOLA & SURROUNDING AREAS IN NANDED GA (Section No-04)
Tender No: MNGL/CP/2024-25/109
Do you want to quote for this sheet ? |  |  | Yes
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE / SCHEDULE OF RATES (SOR) (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Rate inclusive of all taxes and duties except Goods & Service Tax (Rs.) | Per Unit Goods & Service Tax (GST) In % (To be entered by the Bidder) | GST in Rs. | Unit rate inclusive of all taxes & duties including GST (Rs.) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | CARBON STEEL PIPES | Item1
2 | PIPELINE LAYING / INSTALLATION in all type of surface (Normal/built-up surface) "Receiving and taking over" as defined in the specifications, handing, loading, transportation and unloading of Owner supplied 3-Layer PE coated linepipes from Owner's designated stack-yard to Contractor's stock yard/workshop/work-site including preliminary activities, preparation of drawings, wherever required for crossing etc. including handling, stacking, stringing on the pipeline Right-of-Use/ pipeline route alignment, carrying out inspection of company supplied materials including linepipes at the time of taking over, laying/ installation of coated linepipes, associated burried valves, barred tees, insulating joints, flanges & fittings of all sizes, thickness & ANSI class rating and accessories as per specification wherever required depending on site condition including execution of all works, "taking over", handling , including loading and unloading, transportation of Owner supplied materials other than linepipe from Owner's designated place (s) of issue to work site, | Item2
3 | additional lands required for Contractor's storage, fabrication, access for construction, procurement and supply of all materials (except Owner supplied materials), consumables, equipment, labour and other inputs, carrying out all temporary, ancillary, auxiliary works, aquistion of ROU/ROW for laying of pipeline from HDD Exit and entry point to Tie in Point of existing Pipeline/ ROU, ready for commissioning of pipeline as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge, including but not limited to carrying out the following works: | Item3
4 | Surveying of route and detours required at the time of execution including marking the same in topographical sheet, preparation of construction drawings showing survey details, and submit same to Owner for review / approval. | Item4
5 | Staking and installation of construction markers, clearing, fencing, grubbing, cutting of trees, full filling all the requirements of various statutory/ environment authorities to the entire satisfaction of concerned authorities, grading of work area. Shifting of all obstruction within the ROU/ Pipeline route alignment viz. electrical lines/ poles, telephone line / poles, etc. coordination with concerned authorities and obtain permissions from these authorities. | Item5
6 | Trenching to all depths by excavation in all types of soils including soft/ hard rock and different type of pavement / footpath / roads etc. including rock breaking, chiselling or otherwise cutting etc. as required and storing excavated soil, reusable materials at designated area as directed by Engineer in charge and to a width to accommodate the Steel pipeline and MDPE as per the relevant standard/ specification etc. [The minimum depth of the top of pipeline shall be 1.2m measured from top of pipeline coating to the top of undisturbed surface of the soil or as per SCC/ OISD - 141 / 226, whichever is higher]. Dewater of trenches if required as per site condition. | Item6
7 | Carrying out repairs of pipe defects/ replacement in case of irreparable defects and repairs of defects of pipe coating not attributable to Owner including defects/ damages occurring during transportation / handling. | Item7
8 | Stringing of line pipes along pipeline trench / ROU on straw / sand / soft soil bags including supply of bags and its filling materials. | Item8
9 | Checking, cleaning, aligning, bending, cutting and bevelling (as required) of pipes for welding and field adjustments including pipe fittings, welding, carrying out non-destructive testing of welds as required including 100% radiography by X-ray and providing all requisite equipment, labour, supervision, materials, films, consumables, all facilities and personnel to process, develop, examine and interpret radiographs and other tests as required, carrying out repairs of weld joints found defective by Engineer-in-Charge, carrying out re-radiography and other tests as required on repaired joints. | Item9
10 | Carrying out installation of carrier line pipe at all minor crossing viz. carttrack, pathway, water bodies etc. at designated depth by open cut (except at crossing by HDD method). | Item10
11 | Carrying out installation of carrier line pipe in the casing pipe at cased crossing (excluding installation of casing pipes which is covered separately). | Item11
12 | Coating of field weld joints, long radius bends (R=3D), elbows, buried fittings and valves etc. including supply of coating materials etc. (i.e. heat shrinkable sleeves and high build epoxy etc.) as per PJS & Technical Specification compatible with 3 layer PE coating material of the line pipe. | Item12
13 | Counting the number and type of trees cut in presence of DFO/concerned authorities and keeping record thereof, stacking and handing over of all cut tress. | Item13
14 | Installation / lowering the pipeline in trench to required depth as per PJS, Techanical Specification & drawings, supply & placement of 1.0mm thk. HDPE Yellow colour warning mat,RCC tiles (300 mm width x 50 mm thick) over the pipeline & MDPE Pipe in same trench along the complete route as per standard drawings, data sheets & technical specifications, padding around pipeline as per Standard Drg. no. MNGL/Plng./Steel/03 with suitable soil duly approved by EIC including supply of padding material, backfilling and its compaction to the satisfaction of concerned authorities with excavated earth / borrowed select soil including supply of borrowed select soil duly approved by EIC before backfilling and make ready for restoration to be done by Onwer / concerned authorities. | Item14
15 | Supply and installation of slope breakers, wherever required or, as directed by Onwer / Engineer–in–charge. | Item15
16 | Crossing the all-foreign pipeline / HT line / cable / any other utilities etc. with necessary concrete / HDPE sheet protection including coordination with all agencies and obtaining NOC | Item16
17 | Supply and installation of bank protection alongwith backfill materials duly approved by EIC for pipeline trench and banks falls under minor water body crossing as per technical specification & Std. Drg. No. MNGL/Plng./Steel/28, wherever required or, as directed by Onwer / EIC. | Item17
18 | Training and diversions of streams in steep slope area, wherever required. | Item18
19 | Carrying out air cleaning, pigging, flushing, cleaning and hydrostatic testing of complete pipeline with required quantity of corrosion inhibitor including pre-testing of designated sections complete as per specification and approved by Engineer–in–charge to specified pressures indicated elsewhere and duration after stabilization as per specification, providing all equipment, pumps, fittings, instruments, dead weight tester, pressure recorder, thermocouples etc., and services, supervision, labour, consumables, water including supply of corrosion inhibitor, air, etc. as required, locating of leaks and rectification of defect attributable to Contractor (rectification of defects in linepipe material not attributable to contractor shall be paid separately as per other item of schedule of rate), re-testing after rectification, dewatering after successful completion of hydrotesting of entire section and as per specification | Item19
20 | All tieing-in, including the tie-in(s) of the pipeline with the adjacent sections of pipeline including cutting of test header, rebevelling as required, radiography and other NDT examination, joint coating as per specification. | Item20
21 | Final clean-up of right-of-use or area disturbed by contractor during their construction activities for laying of pipeline works and disposal of debris and surplus material to designated disposal areas and backfilling of trench and compaction of the same as per satisfaction of Owner and / Or as directed by Engineer–in–charge. | Item21
22 | Installation of all burried valves (except extended stem valves) inside the valve pit and making provision to operate the valve. | Item22
23 | Preparation of as-built drawings, pipe-books (1 set of tracing on polyester film and 6 sets of as-built drawings and 1 soft copy and 6 hard copies of pipe book) All the works shall be executed in accordance with the provision of contract including carrying out all temporary/ ancillary/ auxiliary works required for the performance of the works and all other acts, deeds, matters and things necessary to make the pipeline ready for precommissioning activities. | Item23
24 | Raking up of hard surface of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. Payment for cutting of hard rock, if any, is covered unders SOR no. 96 | Item24
25 | Specified dia Thk (mm) Material Coating Type Length of each pipe (mm) NB | Item25
26 | 305 (approx.) 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item26 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
27 | 150 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item27 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
28 | 100 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item28 | 1180 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
29 | Note: This item shall be applicable for the underground steel grid main pipeline & branch pipeline, barred tees, insulating joints, bends, flanges & fittings, accessories etc. (i.e. including arrangement for making provision for tap-off on proposed steel grid main pipeline) and aboveground approach pipeline upto Insulating Joint (excluding installation of aboveground insulating joint) for various stations. | Item29
30 | Items except above are covered separately. The lengths of pipelines are tentative. | Item30
31 | Permission Liasioning /Follow-up | Item31
32 | Liasioning & follow up for Permission with all the concerned authorities & boards viz Railways, NH, PWD, MIDC, Local Municipal, Panchyat, Electricity, REC, RES, Sewage water, Drinking water, Forest, Social Forestry, Owners of OFC, Traffic, Law & Order, Fire Brigade, Private Land Owner etc. for entire pipeline length and associated terminals (like SVs, tap-offs) alongwith associated work as per tender. | Item32 | 7700 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
33 | Laying of RCC Tiles | Item33
34 | Providing single layer of RCC Tiles with supply of RCC Tiles to entire width of trench above Warning Mat placed in trench over the laid pipeline as per standard drawing, specification and instruction of Owner. (Rate to include cost of all labour, tools, tackles, equipment, hire charges & supply of all materials, etc.) | Item34
35 | For width of 12" pipeline trench | Item35 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
36 | For width of 6" pipeline trench | Item36 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
37 | For width of 4" pipeline trench | Item37 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
38 | Barricading to comply with HSSE | Item38
39 | Steel barricading of the trenches Cautionary Sign Boards and lighting arrangement shall be provided as per attched drawing no.MNGL/Plng./steel/04. The rates include barricading of trenches along with sign boards, lighting etc. and maintain the same till the back filling of the trench. Rates will be payable per metre of BARRICADING PROVIDED. If proper barricading is not provided, MNGL will barricade the trenches at the risks and costs of the CONTRACTOR and will levy penalty of twice the rate per unit for the relevant section of the pipeline apart from other actions as per contract. | Item39 | 7700 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
40 | RESTORATION OF ROADS Restoration of asphalt / concrete / red stone roads / pavement/Footpath/Paver block including compaction of soil, to original condition as per requirement and to the entire satisfaction of EIC and / or concerned Owners having jurisdiction for following thickness. | Item40
41 | Restoration of Asphalt road upto 10 cm thickness | Item41 | 800 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
42 | Restoration of Asphalt road beyond 10 cm upto 20 cm thickness | Item42 | 200 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
43 | Restoration of Concrete road upto 10 cm thickness | Item43 | 800 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
44 | Restoration of red stone road / footpath / pavement/ Paverblock upto 4 cm thickness | Item44 | 700 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
45 | BORROWED SELECT SOIL FOR BACKFILLING Additional work over and above item 1.0 for supply of specified and approved quality of borrowed soft graded soil / sand in place of available excavated material and / or other suitable soil as per applicable standards / specifications, including backfilling of excavated trench for specified length after laying and padding of pipeline, including transportation of such special backfill material over all distances, complete. | Item45 | 900 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
46 | CROSSING OF STEEL PIPELINE BY OPEN CUT | Item46
47 | Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insatllation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed. | Item47
48 | Road Crossing By Open Cut Method Road Crossings at various locations by Open cut Method along with laying of MDPE upto 180 mm Dia if necessary as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item48
49 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item49 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
50 | Line pipe detail 6" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item50 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
51 | Line pipe detail 4" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item51 | 60 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
52 | Water body Crossing By Open Cut Method water/ canal/ nallah/ drain/ channel Crossings at various locations by Open cut Method along with laying of MDPE upto 180 mm Dia if necessary as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item52
53 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item53 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
54 | Line pipe detail 6" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item54 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
55 | Line pipe detail 4" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item55 | 60 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
56 | Note: Laying of the pipeline by the approved method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item56
57 | Backfilling of the Road/water/ canal/ nallah/ drain/ channel Crossings/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority. | Item57
58 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item58
59 | CROSSINGS/LAYING ALONG THE ROAD BY HDD METHOD | Item59
60 | Complete work of the any crossing (between the limits are defined as approved drawings) by HDD method including "Receiving and taking over" owner supplied three layer PE coated line pipes from Owner's designated place to issue/ dump site(s) and transportation to Contractor's stock yard/ work shop/ work site including all handling loading, unloading, aligning etc. supply of all Contractor supplied material, manpower, equipment, other resources and aquiring the required land for storage, fabrication inclduing string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type Heat Shrink Sleeve and repair of pipeline coating with special repair patch materials as per specification,pre-testing etc. of complete string made for crossing access for Contractor etc and execution of, but not limited to, following works in accordance with specifications scope of work and instructions of Engineer-in-charge and as per all provision of Contract Document. | Item60
61 | Pre-construction surveys based on site visit, collection of historical data from irrigation/ concerned department including design & calculation and detail engineering and making of crossing drawing for getting their approval from concerned Authority/ Engineer-in-charge, getting work permit/ NOC for water crossings/ road crossings as well as utility crossings (if any) encountered during crossing prior to start the execution of work. | Item61
62 | Directional drilling to required depth from top of road including maintenance of drill hole in all types of strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) at all depth to accommodate the pipeline at all conditions encountered during rail/ road crossing by approved HDD methods for providing minimum cover specified in code/ specification or the actual depth as decided by concerned authority, whichever is more. | Item62
63 | In case of water crossing, drilling to the required depth on the banks and bed including maintenance of drill hole in all types of soil strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) all depth to accommodate the pipeline a by HDD methods for providing with minimum cover over top of the pipe at all point across the maximum possible width of water bed (as per drawing) either 1.5 mtrs. below the predicted scour profile expected during the life time of the pipeline or 2.5 mtrs. below the available lowest firm bed (if scour profile/ depth not available) of the water crossing by ascertaining bed level upto 50 mtrs. both the side from crossing location or the actual depth as decided by concerned Authority/ Engineer-in-charge whichever is more. | Item63
64 | Laying of the pipeline by the approved HDD method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints with special type Dirax Heat Shrink Sleeve or equivalent and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item64
65 | Backfilling of the ditch/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority and all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specification, approved drawings, calculations, methods and to the satisfaction of Engineer-in-charge and/or as directed by concerned Authority. | Item65
66 | Post installation hydrotest dewatering and tie-in with pipeline at either side of crossing/banks etc. | Item66
67 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item67
68 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 (along with laying of 4'' Steel Pipe for MDPE if necessary) by HDD Method . | Item68 | 120 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
69 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 150 mm NB x 6.4 mm thk. of API X-52 (along with laying of 4" Steel Pipe for MDPE if necessary) by HDD Method. | Item69 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
70 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 100 mm NB x 6.4 mm thk. of API X-52 (along with laying of 4" Steel Pipe for MDPE if necessary) by HDD Method. | Item70 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
71 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item71 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
72 | Laying along the Road by carrier pipeline of size 150 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item72 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
73 | Laying along the Road by carrier pipeline of size 100 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item73 | 40 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
74 | Installation of carrier pipes by rock drilling for Road/water/Canal/ nallah/ drain/ channel/along the road, or wherever required in all types of hard rock. It includes survey of the underground utilities, submission of profile for approval, execution of the work as per the standard procedure, including , excavation of the pits, insertion/pulling of the carrier pipe, removal of malba, subsequent backfilling and restoration of the facility crossed as per original condition, including supply of all other materials, equipment, consumables, manpower etc including string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type of Heat Shrink Sleeve (Direx) and repair of pipeline coating with special repair patch materials as per Specification, pre-testing etc. of complete string made for crossing/ laying access for Contractor etc. and execution of, but not limited to, following works in accordance with specifications and instruction of Engineer-in-Charge and as per all provision of Contract Document. Balance activities as defined in SOR Item of open trench. Note:The length of HDD mentioned is tentative and may vary to the considerable extent depending upon requirements as per site conditions. The length mentioned in SOR is indicative for all the crossing to be done by HDD, numbers and locations shall be decided by Engineer-in-Charge depending upon site condition. Payment for the length of final tie-in carrier pipeline string with mainline laid by HDD are inclusive in this above item rate. No separate payment shall be made under other clauses mentioned elsewhere. Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item74
75 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 (along with laying of 4'' Steel Pipe for MDPE if necessary) by HDD Method . | Item75 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
76 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 150 mm NB x 6.4 mm thk. of API X-52 (along with laying of 4" Steel Pipe for MDPE if necessary) by HDD Method. | Item76 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
77 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 100 mm NB x 6.4 mm thk. of API X-52 (along with laying of 4" Steel Pipe for MDPE if necessary) by HDD Method. | Item77 | 40 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
78 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item78 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
79 | Laying along the Road by carrier pipeline of size 150 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item79 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
80 | Laying along the Road by carrier pipeline of size 100 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item80 | 40 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
81 | Note: (i) Crossing width & Actual string length for HDD shall vary as per design calculations & site condition so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. | Item81
82 | (ii)Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item82
83 | (iii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by HDD method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item83
84 | (iv) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossing at different locations. | Item84
85 | (v) The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. | Item85
86 | Note: (i) Quantity mentioned under item nos. 48, 52 are indicative only for different location of roads/water/ canal/ nallah/ drain/ channel Crossings. (ii) Actual length & width of individual crossing and cover from top of casing pipe/ carrier pipe string may vary depending upon site condition, approved crossing drawings, specifications etc. and / or as decided by Engineer-in-charge/ Concerned Authority. | Item86
87 | (iii) Payment for supply & installation of Zinc ribbon anode and its design excluded from above item and covered elsewhere in the SOR. (iv) Payment for the length carrier pipeline string inserted in casing pipe laid by Boring are covered separately and shall be paid under other clauses mentioned elesewhere in the SOR. | Item87
88 | Excavation beyond 1.5m depth in case of crossing of utilities/ drain/ culverts etc. through open cut upto the following depth (including restoration of the damaged area to its original condition and satisfaction of the Engineer-in-charge / concerned authorities) : - | Item88
89 | In all type of surface (Kachha/ built-up surface / Hard surface) of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. The other activities are as per SOR 1.1. Payment for cutting of hard rock, if any, is covered unders SOR no. 96 | Item89
90 | Deeper than 1.5 m & upto 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item90 | 800 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
91 | Deeper than 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item91 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
92 | Deeper than 1.5 m & upto 2.5 m below existing level (for 150 (approx.) mm NB Pipeline) | Item92 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
93 | Deeper than 2.5 m below existing level (for 150 (approx.) mm NB Pipeline) | Item93 | 60 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
94 | Deeper than 1.5 m & upto 2.5 m below existing level (for 100 (approx.) mm NB Pipeline) | Item94 | 300 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
95 | Deeper than 2.5 m below existing level (for 100 (approx.) mm NB Pipeline) | Item95 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
96 | Excavation of hard rock | Item96
97 | Excavation of hard rock wherever hard rock of single piece exceeding 1.0 m in length removable by pneumatic chisel/ drill as per direction of EIC. | Item97 | 3800 | Cub. M |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
98 | REPAIR OF COATING DEFECTS (NOT ATTRIBUTED TO CONTRACTOR) | Item98
99 | Repair of Holiday in Coating (Noted and recorded at the time of "receiving and taking over") Supply of all coating repair materials as per requirements of specification to be compatible with line pipe coating material, supply of all consumables, utilities, equipments and all manpower required, pipe cleaning and surface preparation, repairing of coating defects (resulting in holiday) and testing including all handling, transportation, etc. for line pipes, performing all works necessary for the completion of the works stirctly in accordance with relevant specification and instructions of Engineer-In-Charge. This rate shall be applicable per sq. cm of the exposed steel area exposed steel area. | Item99 | 2200 | Sq. cm. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
100 | PERMANENT MARKERS Supply, fabrication and installation of all types of permanent markers along the route including all associated civil works such as excavation in all types of soil, construction in all types of soil, construction of pedestals and grouting with concrete, clearing, supply and application of approved colour and quality of primer and paint, stencil letter cutting for numbers, direction, change etc., restoration of area to original condition and performing all works as per drawing, specification and instruction of engineer-in-charge. | Item100
101 | Pipeline RCC boundary / route marker as per drawing | Item101 | 120 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
102 | Pipeline warning markers with post & foundations | Item102 | 40 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
103 | Pipeline direction marker with post & foundations | Item103 | 25 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
104 | Pipeline KM with post & foundations | Item104 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
105 | HOOK -UP | Item105
106 | Hook-up of proposed pipeline by welding of final tie-in-joint with any existing laid pipeline portion of river X-ing ,existing Tap-off & battery limit of section IV including Hook-up point of the existing pipeline to be made ready for welding by cutting of flanges / valves / headers at all depth in all type of soil etc. Venting of N2 / gas / gas mixture as required purging of N2 Gas (if required), rebevelling as required, radiography and other NDT examination, joint coating as per specification.Contractor shall supply of all consumables, manpower, machinaries, materials, N2 gas etc. and carry out all works as per the provisions of Contract document and instructions of Engineer-in-charge. | Item106
107 | For 12" NB | Item107 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
108 | For 6" NB | Item108 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
109 | For 4" NB | Item109 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
110 | PRE-COMMISSIONING AND ASSISTANCE IN COMMISSIONING OF PIPELINE SYSTEM Swabbing, drying, purging with nitrogen of the complete pipeline network and the associated facilities being installed to the specified acceptance criteria, carrying out pre-commissioning works, providing assistance during the complete duration of commissioning operations for entire pipeline network system including supply of all equipment, man-power, consumables (including pigs & nitrogen required for purging with maintaining nitrogen column of mininum 10% of pipeline geometric volume) materials for all temporary works and performing all associated works, complete as per the relevant specifications, other provisions of Contract document and instructions of Engineer-in-charge. | Item110
111 | For 12" NB Pipeline | Item111 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
112 | For 6" NB Pipeline | Item112 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
113 | For 4" NB Pipeline | Item113 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
114 | IDLE TIME PRESERVATION OF PIPELINE Preservation of complete pipeline and associated facilities forming part of the pipeline as per Bid document and its maintenance including supply of all consumables, all equipment, manpower, etc. complete as per the requirements of specifications, other provisions of Contract document and instructions of Engineer-in-charge. Note : Owner reserves the right to exercise either or none of the rates below. | Item114
115 | By filling and pressurizing with nitrogen to a pressure of 2 bar(g) for a period of 3 months. | Item115
116 | For 12" NB Pipeline | Item116 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
117 | For 6" NB Pipeline | Item117 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
118 | For 4" NB Pipeline | Item118 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
119 | For every additional period of one month or part thereof | Item119
120 | For 12" NB Pipeline | Item120 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
121 | For 6" NB Pipeline | Item121 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
122 | For 4" NB Pipeline | Item122 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
123 | RCC VALVE PITS All civil works including supply of all materials, excavation of pit, piping supports including all PCC and RCC works for valves pits including pedestals with insert plates as required sealing of pipe at valve pits, providing cover etc. and finishing , clean-up and restoration of site, filling and grading of area around valve station for avoiding any local flooding of area, as per typical drawing and specification enclosed and instructions of Engineer-in-charge. In this item, instead of Brick Work, RCC will be done | Item123
124 | Valve Pit of Size 2m x 2m | Item124 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
125 | Valve Pit of Size 1.5m x 1 m | Item125 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
126 | Valve Pit of Size 1 m x 1 m | Item126 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
127 | SUPPLY OF ASSORTED PIPE, FITTINGS AND FLANGES Complete works of supply of pipes, flanges & fittings for aboveground & underground installation including all taxes, duties, transportation and inspection charges but not limited to, the following items in accordance with PMS (piping material specification), relevant specifications & drawings indicated in job specification under SCC (technical) and instructions of Engineer-in-charge and as per all provisions of the CONTRACT DOCUMENT. - Handling including lifting, transportation from Contractor Stores to CONTRACTOR's workshop for fabrication and/ or to work site for field fabrication and erection for all piping items supplied by Contractor. | Item127
128 | Carbon Steel Pipe (A 106, Seamless B-36.10/ API X 52 ) | Item128
129 | Size Rating/ Schedule | Item129
130 | 2" NB, BE Sch. 80 | Item130 | 55 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
131 | 1" NB, PE Sch. 80 | Item131 | 38 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
132 | ¾" NB, PE Sch. 160 | Item132 | 32 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
133 | Flanges | Item133
134 | Weld Neck (B-16.5, 300# A105,125 AARH, Serrated finish) | Item134
135 | Size Rating/ Schedule | Item135
136 | 6" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item136 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
137 | 4" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item137 | 5 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
138 | 2" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item138 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
139 | 3/4" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item139 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
140 | Blind Flanges (B-16.5, 300# A105,125 AARH Serrated) | Item140
141 | Size | Item141
142 | 6" NB, RF | Item142 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
143 | 4" NB, RF | Item143 | 5 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
144 | 2" NB, RF | Item144 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
145 | 3/4" NB, RF | Item145 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
146 | Elbow (Seamless) | Item146
147 | 90° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item147
148 | Size Rating/ Schedule | Item148
149 | 12" NB 300# | Item149 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
150 | 6" NB 300# | Item150 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
151 | 4" NB 300# | Item151 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
152 | 2" NB Sch. 80 | Item152 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
153 | 45° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item153
154 | Size Rating/ Schedule | Item154
155 | 12" NB 300# | Item155 | 22 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
156 | 6" NB 300# | Item156 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
157 | 4" NB 300# | Item157 | 10 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
158 | 2" NB Sch. 80 | Item158 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
159 | 90° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item159
160 | Size Rating/ Schedule | Item160
161 | 12" NB 300# | Item161 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
162 | 6" NB 300# | Item162 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
163 | 4" NB 300# | Item163 | 10 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
164 | 45° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item164
165 | Size Rating/ Schedule | Item165
166 | 12" NB 300# | Item166 | 22 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
167 | 6" NB 300# | Item167 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
168 | 4" NB 300# | Item168 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
169 | 22½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D) Min Thickness 6.4mm | Item169
170 | Size Rating/ Schedule | Item170
171 | 12" NB Sch. Std. | Item171 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
172 | 6" NB End thickness to match with pipe wall thickness | Item172 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
173 | 11½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D), Min Thickness 6.4mm | Item173
174 | Size Rating/ Schedule | Item174
175 | 12" NB 300# | Item175 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
176 | 6" NB 300# | Item176 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
177 | Tees (Seamless) | Item177
178 | Equal Tee (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item178
179 | Size Rating/ Schedule | Item179
180 | 12" NB x 12" NB x 12" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item180 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
181 | 6" NB x 6" NB x 6" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item181 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
182 | 4" NB x 4" NB x 4" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item182 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
183 | 2" NB x 2" NB x 2" NB Sch. XS | Item183 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
184 | Unequal Tee (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item184
185 | Size Rating/ Schedule | Item185
186 | 12" NB x 12" NB x 6" NB Sch. Std. x Sch. Std. | Item186 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
187 | 12" NB x 12" NB x 4" NB Sch. Std. x Sch. Std. | Item187 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
188 | 4" NB x 4" NB x 2" NB Sch. 80 x Sch.80 | Item188 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
189 | 6" NB x 6" NB x 4" NB Sch. Std.x Sch. XS | Item189 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
190 | Reducer (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item190
191 | 12" NB x 6" NB Min Thickness 6.4mm | Item191 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
192 | 12" NB x 4" NB Min Thickness 6.4mm | Item192 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
193 | 6" NB X 4" NB Min Thickness 6.4mm | Item193 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
194 | 4" NB X 2" NB Min Thickness 6.4mm | Item194 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
195 | Weldolet and Sockolet | Item195
196 | Weldolet (MOC A105 & DIM. MSS SP 97) | Item196
197 | Size Rating/ Schedule | Item197
198 | 12" NB x 2" NB Sch. 80. | Item198 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
199 | 6" NB x 2" NB Sch.80 | Item199 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
200 | 4" NB x 2" NB Sch. 80 | Item200 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
201 | Sockolet (MOC A105 & DIM. MSS SP 97) | Item201
202 | 12" NB x 3/4" NB #6000 | Item202 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
203 | 6" NB x 3/4" NB #3000 | Item203 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
204 | 6" NB x 1" NB #3000 | Item204 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
205 | 4" NB x 3/4" NB #3000 | Item205 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
206 | Butt Weld Disc End Cap (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item206
207 | Size Rating/ Schedule | Item207
208 | 12" Sch. Std. | Item208 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
209 | 6" Sch. 40 | Item209 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
210 | 4" Sch. 80 | Item210 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
211 | Fabrication & Installation of Underground Valve Assembly | Item211
212 | 12"NB Isolation Valve/tap-off assembly as per Drg. No. MNGL/Plng./Steel/40 | Item212 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
213 | 6" NB Isolation Valve/tap-off assembly as per Drg. No.MNGL/Plng./Steel/40 | Item213 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
214 | 4" NB Isolation Valve/tap-off assembly as per Drg. No. MNGL/Plng./Steel/40 | Item214 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
215 | Note: | Item215
216 | For all the supply items mentioned above, procurement shall be made as per enclosed Data Sheets and respective technical specification, after due approval of Engineer-in-charge. | Item216
217 | The quantities mentioned above are tentative and quantities for above supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item217
218 | PLANT PIPING (ABOVEGROUND) Fabrication and testing of carbon steel piping and fittings, valves, IJ, including supply of all consumables, equipment, manpower, and other resources and execution of job as per instruction AIC/EIC.Transportation of all piping items from Owner's and/ or Contractor's storage point to work at site/ workshop as applicable, complete work of fabrication, erection, painting, testing of pipes, flanges and fittings and making ready for further Commissioning / Start-up of carbon steel piping of all sizes and ratings including supply of all consumables, equipment, manpower and other resources and execution of, but not limited to, as per all provisions of the CONTRACT DOCUMENT. | Item218
219 | Fabrication including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site, cutting, edge preparation, inclusive of grinding the edges of pipes, fittings, flanges, reducers etc. to match with the matching edges of uneven thickness, wherever required, fit-up, welding of pipes and fittings like elbows, tees, reducers, weldolets, sockolets, Valves, IJ etc. flanges, vent and drain point connection, Radiography and NDT of all joints etc, including providing stubin connections, fabricated fittings and reinforcement pads etc., as required. | Item219
220 | Erection of pipes of all types and thickness at all elevations, connecting with equipment nozzle, aligning, installation and carrying out connected activities for all types of valves, all online instruments and fittings of all sizes of elbow, reducers, tees, flanges, blind flanges, spectacle blind flanges, branch connection / tapping for pressure gauges, including installation of gaskets and bolts. | Item220
221 | Erection including prior cleaning, lifting, placing on pipe sleepers and supports, overhead on racks, skids and at all elevations including installation and carrying out connected activities for all types of valves including supply and fixing of gaskets, studs/ bolts, nuts wherever required for all sizes, levelling, aligning, joining of flanges, blind flanges, connecting with equipment, nozzles, strainers, tie-in with existing piping/facilities, etc. tapping for inline instruments like pressure gauges, thermowells, sample connection, etc. | Item221
222 | Hydro testing of the piping job shall be conducted at pressure mentioned in specification for a period of 4 hours by using de-mineralised water, to check its strength. No visible leakages shall be detected during the test. Testing shall be conducted as per tender specification. | Item222
223 | Preparation of final bill of material based on piping GADs. | Item223
224 | Preparation of isometric and fabrication drawings. | Item224
225 | Carrying out Non-destructive testing as required except items mentioned in sl. no. 286 of SOR. | Item225
226 | Painting of entire system (including aboveground all pipes fittings, flanges and accessories) as per specifications suitable for highly corrosive area environment including supply of approved paints and primers, application of primer and paints, indentification lettering/ numbering, colour coding, etc. as specified including rub down & touch up of shop primer or scrapping of shop primer wherever required by COMPANY and providing scaffolding for all heights etc. | Item226
227 | Cleaning and flushing by water/ compressed air, testing of the systems including hydrostatic, pneumatic and any other type of testing as specified, draining, drying by compressed air/other methods approved by COMPANY. | Item227
228 | Precommissioning & making operational all piping system and equipments. | Item228
229 | Commissioning Contractor scope shall provide all necessary assistance in term of supply of man-power, equipment, tools and tackles required amount of nitrogen for purging of entire terminal piping system including equipments etc. to the company during commissioning activities. | Item229
230 | Completion of all such work in all respects as per scope of work and as per drawings, specifications and instructions of the COMPANY and keeping the system ready in all respects for further commissioning and start up. | Item230
231 | Hook-up works (with client/ consumer piping at battery limits): | Item231
232 | Complete Carbon Steel aboveground Piping Work with painting including all fittings, flanges and supply of all required gaskets, studs bolts & nuts etc. and Any other work and material required for the completion of the work and not covered above and desired by EIC shall be in the scope of contractor | Item232
233 | Carbon Steel Pipe (ASTM A 106, Seamless B-36.10 / API X 52) | Item233 | 250 | inch Dia |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
234 | 1) Pipe Specification and thickness may vary depending upon availability of pipe. No extra payment shall be made for this. 2) All butt welded fittings & flanges end shall generally match with connecting pipe wall thickness. However, in case of misalignment, Contractor shall have to do end preparation without any extra cost. 3) All o-lets less than 2" NB size, all sizes of coupling and nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under erection rate. | Item234
235 | Aboveground installation of Insulating Joint & Valves etc. Handling including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site and installation of all types of valves, insulating joint including assembly of valve accessories, (if any) by bolting, threading or welding, supply and insertion of gaskets, nuts & bolts, nipples, etc. at all elevations of pipe sleepers, supports or overhead on racks, equipments nozzle, skid & painting etc. supply of all consumables, manpower, equipment, etc. for completion of all works as per scope of work and as per drawings, specifications and instructions of Engineer-in-charge including servicing/ cleaning of valve wherever requried. | Item235
236 | Welded Valves (Full Bore/ Reduced Bore) Ball / Globe / Check Valve | Item236
237 | Size Rating/ Schedule | Item237
238 | 4" NB 300# | Item238 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
239 | 2" NB 300# | Item239 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
240 | Sockolet Welded Valve (Ball / Globe Valve) | Item240
241 | Size Rating/ Schedule | Item241
242 | 1" NB 800# | Item242 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
243 | ¾" NB 800# | Item243 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
244 | 12" NB, 300# - Insulating Joints | Item244 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
245 | 6" NB, 300# - Insulating Joints | Item245 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
246 | 4" NB, 300# - Insulating Joints | Item246 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
247 | STRUCTURAL WORKS | Item247
248 | Supply of erection of single leaf mild steel gate 2.5m high with mesh upto 2m height and barbed wire fencing and 2m wide complete in all respect including painting as per TS on all MS items, all works as per specification and drawings excluding foundations and RCC beams. | Item248 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
249 | Supply of all materials, fabrication and erection of chain link fencing 2.5m high with mesh up to 2m height and barbed wire fenching complete in all respects including painting as per TS on all MS items, all works as per specification and drawings excluding foundation and RCC beams. | Item249 | 150 | RM |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
250 | Pipe Supports & Other Structures | Item250
251 | Supply, fabrication and erection of all types of pipe supports like clamps, saddle, guide stops, cradles, turn buckles, anchors, T-posts; stockade/ trestle and pipe bridge for overhead piping; frames for canopy, approach ladders and platforms, crossover, cable tray supports, etc. including painting suitable for highly corrosive area as per specification labour and supervision & complete work as per drawings, specifications and instruction of Engineerqw-incharge. (Bolts, nuts, washers, U-clamps etc. for supporting shall be supplied by the Contractor within the rates quoted. These items will not be measured and paid seperately). The work is to be completed in all respect as per scope of work and specification. | Item251 | 300 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
252 | Notes: | Item252
253 | The quantities indicated are estimated values and hence are approximate. Final payment will be made based on actual quantities to be certified by the Purchaser. | Item253
254 | The cost of MS bolts (permanent and service(, washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants etc., as required for the work shall be deemed to be included in the quoted rates. | Item254
255 | All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accrodance with time schedule, are deemed be included in the quoted rates. | Item255
256 | CIVIL WORKS | Item256
257 | Site Grading Excavation in earth and filling to the grades and levels shown in the approved drawings in all kinds of conditions including for Road embarkments, using approved quality good earth from designated borrow area, for all heights and depths including clearing and stripping (min. 150mm) of the area marked for filling, taking spot levels, consolidating the exposed natural soil surface, excavating the earth from borrow area loading, transporting & unloading, spreading in layers not exceeding 150mm thickness, breaking clods, watering (if reqd.), ramming and compacting by manual/ mechanical means to give minimum 92% of modified Proctor's density of earth, testing & dressing including disposal of all unserviceable material all complete as per specifications and directions of Engineer-in-charge. | Item257 | 150 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
258 | (Rate to include cost of all labour, tools, tackles, equipment, hire charges, cost of borrow earth by way of royalties, right of way, cess etc., as applicable with all bye works and sundry works). | Item258
259 | Plain Cement Concrete Supplying and laying plain cement concrete (including shuttering of required) in all types of concrete works including levelling courses below foundation, substructure, superstrcuture, chambers, cable tranch, under floors and any other locations, at all leveies as per drawings, specifications and directions of the Engineer-in-charge. | Item259
260 | PCC 1:2:4 1 Cement : 2 Coarse sand : 4 stone aggregate 20mm nominal size. | Item260 | 400 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
261 | Reinforced Cement Concrete Providing and laying reinforced cement of grade M-20 with 20mm and down grade crushed stone aggregate in all types of structures like foundations, pedestals, pedestal bases, pipe supports, sleepers cable trench inlcuding constrcution joints, bitumen painting on surface in contact with soil, providing and fixing reinforcing steel, shuttering, inserts, finishes etc. at all depths and heights complete as per drawings, specifications and direction of the Engineer-incharge. | Item261 | 300 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
262 | Rate to include cost of all labour, tools, tackles, equipment, hire charges, supply of all maerials such as minimum 43 grade cement including sulphate resistant cement for substructures, R/F steel, Inserts, bolts, conduits, bitumen, other minor constrcution materials, shuttering, stanging, earthwork in excavation and backfilling using serviceable earth in all conditions, shorting bailing and pumping out water, testing of concrete, curing etc. with all bye works and syndry works. | Item262
263 | TEMPORARY CATHODIC PROTECTION SYSTEM | Item263
264 | Design, detailed engineering, supply, installation, testing and commissioning of the temporary Cathodic protection system using Mg/ Zn galvanic anodes to protect the external surface of 3 LPE coated entire 5.5 km (approx.) long steel pipeline network against corrosion for design life of minimum 1 year or till commissioning of PCP system whichever is later as per standard specification No. MNGL/Steel/TS/15 for temporary cathodic protection system. Scope shall also include but not limited to the following for completion of jobs: | Item264
265 | Measurement of soil resistivity along the right of way of the main pipeline route as per specification for design & installation of anodes. | Item265
266 | Collection of additional data related to cathodic protection along the right of way of pipeline as per specifications. | Item266
267 | Supply, installation, testing & commissioning of one set of spark gap arrestor with 2 plate Zinc grounding cell of 20 kg net weight each across each insulating joint as per specification. | Item267
268 | Supply, installation, testing & commissioning one set of polarisation cell with zinc anode at all high tension (66KV or higher) electrical power transmission line/Equipment crossing or running parallel to the pipeline for grounding purpose as per specification. The rating shall depend upon anticipated fault current & ground bed resistance at the location of installation. However, the rating of polarisation cell (krick) shall not be less than 5 KA & number of 20 kg net weight zinc anode shall not be less than two. | Item268
269 | Supply & installation of Zinc Ribbon Anodes at 4-8 O’Clock position in the interval of 2 metre (max.) on carrier pipes at all cased crossings i.e. railways/ roads etc. | Item269
270 | Monitoring of the protection system for 6 months. | Item270
271 | All civil/ structural works related to TCP system including supply of bricks, cement & steel etc. required for completion of the system. | Item271
272 | For 12" | Item272 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
273 | For 6" | Item273 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
274 | For 4" | Item274 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
275 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item275
276 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item276
277 | FIELD INSTRUMENTATION | Item277
278 | PRESSURE INSTRUMENTS | Item278
279 | Supply , Installation of Pressure Gagues and their accessories inclusive of supply of necessary piping materials and tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/ manifolds & hydraulic testing (exclusive of calibration of instruments) as per installation standard attached elsewhere in Tender Document and Supply as per Data Sheet No.MEC/23K8/05/E5/I/001/DS-PG. Give breakup of supply and Installation rate. | Item279 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
280 | CALIBRATION | Item280
281 | Calibration of the instruments listed below including removal of instruments from pre-installed locations like panels, enclosure racks, fields etc. and refixing them back in respective/ required places, providing equipments, necessary test jigs, instrument air and all consumables. Calibration reports shall be prepared and to be submitted to the Purchaser/ Consultant. | Item281
282 | Pressure Gauges | Item282 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
283 | Note: | Item283
284 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item284
285 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item285
286 | Laying of MDPE pipe along with Steel pipe line Excluding supply of all MDPE pipe (PE 80/100,SDR11), but Including supply of Bends, Couplers, End caps, Tees, PE Reducer, CS to PE Fitting, Saddle Tapping, Warming mat, etc. as required to complete the job. ( Particular job specification.) "Receiving and taking-over" as defined in the specification, handling, loading, transportation and unloading of Owner supplied MDPE line pipes (PE80/100, SDR11) of all sizes (as free issue items) from Owner's designated place(s) of issue to Contractor's own stock-yard(s)/ Work Shop(s)/ work-site(s) including proper storing, stacking, identification, providing security & insurance cover , including supply of accessories of all sizes & thickness like Bends, Couplers, End caps, Tee, PE Reducer, CS to PE Fittings, Saddle Tapping, Warning Mat, etc.. | Item286
287 | Stringing/ uncoiling of the MDPE line pipe on the pipeline Right-of-Use, laying/ installation of MDPE line pipe alongwith steel pipeline (alongwith installation of required accessories as mentioned above) of following sizes, including executing all works; fabrication, access for construction; supply of all materials (except Owner supplied materials), consumables, labour and other incidental works and handing over the same after return of the surplus pipes to the Owner's designated stockyard(s); carrying out all temporary, ancillary, auxiliary works required to make the MDPE pipeline ready for commissioning as per drawings, specifications, scope of work indicated in PJS and other provisions of Contract document and instructions of Engineer-in-charge. | Item287
288 | UP to Dia 90mm | Item288 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
289 | Dia 125mm | Item289 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
290 | Note : The quantities indicated above against all individual item are tentative and may vary considerably depending upon site condition, methodology adopted as per site requirement with due approval of Owner/ Consultants. | Item290
291 | PIPING WORKS FOR SECTIONALISING VALVE STATION-CUM-TAP-OFF POINT All works for fabriaction and installation of all piping above ground at all elevations and below ground at all depth for Sectionalising Valve Station alongwith preparation of construction drawings duly approved by EIC, in all type of terrains and soils including transportation and handling of all Owner supplied materials i.e. extended stem butt welded sectionalising gas actuated ball valve, other types of valves, line pipes for mainline, 4" NB pipe for all branch line including ventlines from Owner's designated place(s) of issue to work site. | Item291
292 | Contractor shall supply all required size & type of piping material like pipes, fittings & flanges etc. as per PMS alongwith 2" NB pipe for all branch line & vent line (wherever required) including supply of all consumables, manpower, machinaries, materials etc. and carrying out all mechanical works of underground and above ground piping including fabrication, welding, nondestructive testing of welds, weld repairs/ retesting, cleaning/ flushing, pre-hydrotesting & hydrostatic testing, dewatering, functional testing, cutting of mainline and bevelling (if required) | Item292
293 | assembly, including radiography of tie-in joints, corrosion, coating and external painting as required, installation of instruments like pressure/ temperature instruments/ gauges alongwith complete SS Tubing works including supply of SS Tube and thier accessories etc., as required, obtaining all statutory clearances, approvals and permissions for the works (wherever required), making of valve pit (for detail refer relevant drawings) for SV Stationscum- tap-off points enclosed with tender filled with sand, excavation and filling in all types of soils including soft/ hard rock for installation of piping/ pipe supports providing pipe supports, area fencing and gate including all associated civil and structural works; painting, finishing, clean-up and restoration of site; preparation of as-built drawings, documents and project records and performing all works as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge. In this item, instead of Brick Work RCC will be done | Item293
294 | Type - I SV Station on 12" Pipeline | Item294 | 1 | Lumpsum for each |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
295 | Note: i) Work under above items are exclusive of all works associated with main pipeline covered under Item No. 1.0 above. ii) All civil/ structural works including area fencing and gate, valve pits except for piping support will be paid separately as per unit rate provided elsewhere in the SOR. iii) All coupling, nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under above item rate. | Item295
296 | Details of Major Road Crossing (Canal/SH/DR/NHAI): Supply, Installation & Insertion of pipeline across Canal / State Highways as per SCC and technical specifications | Item296
297 | Supply & Installation of 24" NB x 6.4mm Wall thk. Casing pipe for Line Pipe 12"NB(6.4 mm thk API 5L Gr X52) & 4" NB, 6.4 mm thk API 5L Gr. X52 pipe by Jacking Boring . Including Insertion of 12" dia and 4" dia (for 125 mm dia MDPE Connectivity) Carrier pipeline in 24" dia casing pipe and connectivity with existing pipeline at both end of National Highways/State Highways/ Railway as per SCC and technical specifications -Supply of Casing Pipe Supply of following casing pipe including handling, loading, transportation & unloading etc. to contractor's own stock yard / worksite(s). -After Completion of insertion of carrier pipe with Connectivity at both end including all works as per the scope of work -Post Hydro testing & Commissioning , Submission of as-built drawing, Submission of Documents - The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. - Rate Should include supply & installation of 250mm Casing pipe for 4" Steel Pipeline for MDPE (if required by Authority & as per the instructions of EIC) | Item297
298 | Note: (i) Crossing width may vary as per site condition. Tenderer are advised to visit site for actual assessment of extent of crossing. Actual length of Boring shall be as per design calculations so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. (ii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by Boring method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item298
299 | (iii) The Contractor has to quote alongwith 4" NB (for 125mm MDPE). No any extra payment shall be made against this item. (iv) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossings at different locations. | Item299
300 | (v) Actual length & cover from top of casing pipe string may vary depending upon site conditions, approved drawings, specification etc. and / or as decided by concerned Authority / Engineer-in-charge. (vi) No Extra Payment for supply & installation of Zinc ribbon to be provided to Carrier pipe & Zinc Anode is to be provided to Casing pipe and its design included in above item | Item300
301 | Supply and installation of 24'' casing pipe,Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insertion of carrier pipe in casing pipe after above ground pretesting at specified test pressure and installation of casing insulators & Zinc ribbon anode as per specification/ drawings. Installation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed (Any type of soil) | Item301 | 120 | Mtrs |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
Total in Figures | [51 empty] | 0 | 0 | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## BoQ5 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR | [49 empty] | 1
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Maharastra Natural Gas Ltd.,Pune
Name of Work:LAYING & CONSTRUCTION OF 12” NB X 6 KM , 6" NB X 0.2 KM & 4" NB X 1 KM U/G STEEL PIPELINE NETWORK & ASSOCIATED WORKS FROM MAULI AUTO PARTS SHOP NEAR TITVI BRIDGE, PANGRADOLA TO NEAR BHIWAPUR VILLAGE ROAD, BHIWAPUR & SURROUNDING AREAS IN NANDED GA.(Section No-05)
Tender No: MNGL/CP/2024-25/109
Do you want to quote for this sheet ? |  |  | Yes
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE / SCHEDULE OF RATES (SOR) (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Rate inclusive of all taxes and duties except Goods & Service Tax (Rs.) | Per Unit Goods & Service Tax (GST) In % (To be entered by the Bidder) | GST in Rs. | Unit rate inclusive of all taxes & duties including GST (Rs.) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | CARBON STEEL PIPES | Item1
2 | PIPELINE LAYING / INSTALLATION in all type of surface (Normal/built-up surface) "Receiving and taking over" as defined in the specifications, handing, loading, transportation and unloading of Owner supplied 3-Layer PE coated linepipes from Owner's designated stack-yard to Contractor's stock yard/workshop/work-site including preliminary activities, preparation of drawings, wherever required for crossing etc. including handling, stacking, stringing on the pipeline Right-of-Use/ pipeline route alignment, carrying out inspection of company supplied materials including linepipes at the time of taking over, laying/ installation of coated linepipes, associated burried valves, barred tees, insulating joints, flanges & fittings of all sizes, thickness & ANSI class rating and accessories as per specification wherever required depending on site condition including execution of all works, "taking over", handling , including loading and unloading, transportation of Owner supplied materials other than linepipe from Owner's designated place (s) of issue to work site, | Item2
3 | additional lands required for Contractor's storage, fabrication, access for construction, procurement and supply of all materials (except Owner supplied materials), consumables, equipment, labour and other inputs, carrying out all temporary, ancillary, auxiliary works, aquistion of ROU/ROW for laying of pipeline from HDD Exit and entry point to Tie in Point of existing Pipeline/ ROU, ready for commissioning of pipeline as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge, including but not limited to carrying out the following works: | Item3
4 | Surveying of route and detours required at the time of execution including marking the same in topographical sheet, preparation of construction drawings showing survey details, and submit same to Owner for review / approval. | Item4
5 | Staking and installation of construction markers, clearing, fencing, grubbing, cutting of trees, full filling all the requirements of various statutory/ environment authorities to the entire satisfaction of concerned authorities, grading of work area. Shifting of all obstruction within the ROU/ Pipeline route alignment viz. electrical lines/ poles, telephone line / poles, etc. coordination with concerned authorities and obtain permissions from these authorities. | Item5
6 | Trenching to all depths by excavation in all types of soils including soft/ hard rock and different type of pavement / footpath / roads etc. including rock breaking, chiselling or otherwise cutting etc. as required and storing excavated soil, reusable materials at designated area as directed by Engineer in charge and to a width to accommodate the Steel pipeline and MDPE as per the relevant standard/ specification etc. [The minimum depth of the top of pipeline shall be 1.2m measured from top of pipeline coating to the top of undisturbed surface of the soil or as per SCC/ OISD - 141 / 226, whichever is higher]. Dewater of trenches if required as per site condition. | Item6
7 | Carrying out repairs of pipe defects/ replacement in case of irreparable defects and repairs of defects of pipe coating not attributable to Owner including defects/ damages occurring during transportation / handling. | Item7
8 | Stringing of line pipes along pipeline trench / ROU on straw / sand / soft soil bags including supply of bags and its filling materials. | Item8
9 | Checking, cleaning, aligning, bending, cutting and bevelling (as required) of pipes for welding and field adjustments including pipe fittings, welding, carrying out non-destructive testing of welds as required including 100% radiography by X-ray and providing all requisite equipment, labour, supervision, materials, films, consumables, all facilities and personnel to process, develop, examine and interpret radiographs and other tests as required, carrying out repairs of weld joints found defective by Engineer-in-Charge, carrying out re-radiography and other tests as required on repaired joints. | Item9
10 | Carrying out installation of carrier line pipe at all minor crossing viz. carttrack, pathway, water bodies etc. at designated depth by open cut (except at crossing by HDD method). | Item10
11 | Carrying out installation of carrier line pipe in the casing pipe at cased crossing (excluding installation of casing pipes which is covered separately). | Item11
12 | Coating of field weld joints, long radius bends (R=3D), elbows, buried fittings and valves etc. including supply of coating materials etc. (i.e. heat shrinkable sleeves and high build epoxy etc.) as per PJS & Technical Specification compatible with 3 layer PE coating material of the line pipe. | Item12
13 | Counting the number and type of trees cut in presence of DFO/concerned authorities and keeping record thereof, stacking and handing over of all cut tress. | Item13
14 | Installation / lowering the pipeline in trench to required depth as per PJS, Techanical Specification & drawings, supply & placement of 1.0mm thk. HDPE Yellow colour warning mat,RCC tiles (300 mm width x 50 mm thick) over the pipeline & MDPE Pipe in same trench along the complete route as per standard drawings, data sheets & technical specifications, padding around pipeline as per Standard Drg. no. MNGL/Plng./Steel/03 with suitable soil duly approved by EIC including supply of padding material, backfilling and its compaction to the satisfaction of concerned authorities with excavated earth / borrowed select soil including supply of borrowed select soil duly approved by EIC before backfilling and make ready for restoration to be done by Onwer / concerned authorities. | Item14
15 | Supply and installation of slope breakers, wherever required or, as directed by Onwer / Engineer–in–charge. | Item15
16 | Crossing the all-foreign pipeline / HT line / cable / any other utilities etc. with necessary concrete / HDPE sheet protection including coordination with all agencies and obtaining NOC | Item16
17 | Supply and installation of bank protection alongwith backfill materials duly approved by EIC for pipeline trench and banks falls under minor water body crossing as per technical specification & Std. Drg. No. MNGL/Plng./Steel/28, wherever required or, as directed by Onwer / EIC. | Item17
18 | Training and diversions of streams in steep slope area, wherever required. | Item18
19 | Carrying out air cleaning, pigging, flushing, cleaning and hydrostatic testing of complete pipeline with required quantity of corrosion inhibitor including pre-testing of designated sections complete as per specification and approved by Engineer–in–charge to specified pressures indicated elsewhere and duration after stabilization as per specification, providing all equipment, pumps, fittings, instruments, dead weight tester, pressure recorder, thermocouples etc., and services, supervision, labour, consumables, water including supply of corrosion inhibitor, air, etc. as required, locating of leaks and rectification of defect attributable to Contractor (rectification of defects in linepipe material not attributable to contractor shall be paid separately as per other item of schedule of rate), re-testing after rectification, dewatering after successful completion of hydrotesting of entire section and as per specification | Item19
20 | All tieing-in, including the tie-in(s) of the pipeline with the adjacent sections of pipeline including cutting of test header, rebevelling as required, radiography and other NDT examination, joint coating as per specification. | Item20
21 | Final clean-up of right-of-use or area disturbed by contractor during their construction activities for laying of pipeline works and disposal of debris and surplus material to designated disposal areas and backfilling of trench and compaction of the same as per satisfaction of Owner and / Or as directed by Engineer–in–charge. | Item21
22 | Installation of all burried valves (except extended stem valves) inside the valve pit and making provision to operate the valve. | Item22
23 | Preparation of as-built drawings, pipe-books (1 set of tracing on polyester film and 6 sets of as-built drawings and 1 soft copy and 6 hard copies of pipe book) All the works shall be executed in accordance with the provision of contract including carrying out all temporary/ ancillary/ auxiliary works required for the performance of the works and all other acts, deeds, matters and things necessary to make the pipeline ready for precommissioning activities. | Item23
24 | Raking up of hard surface of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. Payment for cutting of hard rock, if any, is covered unders SOR no. 96 | Item24
25 | Specified dia Thk (mm) Material Coating Type Length of each pipe (mm) NB | Item25
26 | 305 (approx.) 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item26 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
27 | 150 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item27 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
28 | 100 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item28 | 640 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
29 | Note: This item shall be applicable for the underground steel grid main pipeline & branch pipeline, barred tees, insulating joints, bends, flanges & fittings, accessories etc. (i.e. including arrangement for making provision for tap-off on proposed steel grid main pipeline) and aboveground approach pipeline upto Insulating Joint (excluding installation of aboveground insulating joint) for various stations. | Item29
30 | Items except above are covered separately. The lengths of pipelines are tentative. | Item30
31 | Permission Liasioning /Follow-up | Item31
32 | Liasioning & follow up for Permission with all the concerned authorities & boards viz Railways, NH, PWD, MIDC, Local Municipal, Panchyat, Electricity, REC, RES, Sewage water, Drinking water, Forest, Social Forestry, Owners of OFC, Traffic, Law & Order, Fire Brigade, Private Land Owner etc. for entire pipeline length and associated terminals (like SVs, tap-offs) alongwith associated work as per tender. | Item32 | 7200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
33 | Laying of RCC Tiles | Item33
34 | Providing single layer of RCC Tiles with supply of RCC Tiles to entire width of trench above Warning Mat placed in trench over the laid pipeline as per standard drawing, specification and instruction of Owner. (Rate to include cost of all labour, tools, tackles, equipment, hire charges & supply of all materials, etc.) | Item34
35 | For width of 12" pipeline trench | Item35 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
36 | For width of 6" pipeline trench | Item36 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
37 | For width of 4" pipeline trench | Item37 | 1000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
38 | Barricading to comply with HSSE | Item38
39 | Steel barricading of the trenches Cautionary Sign Boards and lighting arrangement shall be provided as per attched drawing no.MNGL/Plng./steel/04. The rates include barricading of trenches along with sign boards, lighting etc. and maintain the same till the back filling of the trench. Rates will be payable per metre of BARRICADING PROVIDED. If proper barricading is not provided, MNGL will barricade the trenches at the risks and costs of the CONTRACTOR and will levy penalty of twice the rate per unit for the relevant section of the pipeline apart from other actions as per contract. | Item39 | 7200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
40 | RESTORATION OF ROADS Restoration of asphalt / concrete / red stone roads / pavement/Footpath/Paver block including compaction of soil, to original condition as per requirement and to the entire satisfaction of EIC and / or concerned Owners having jurisdiction for following thickness. | Item40
41 | Restoration of Asphalt road upto 10 cm thickness | Item41 | 700 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
42 | Restoration of Asphalt road beyond 10 cm upto 20 cm thickness | Item42 | 200 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
43 | Restoration of Concrete road upto 10 cm thickness | Item43 | 600 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
44 | Restoration of red stone road / footpath / pavement/ Paverblock upto 4 cm thickness | Item44 | 600 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
45 | BORROWED SELECT SOIL FOR BACKFILLING Additional work over and above item 1.0 for supply of specified and approved quality of borrowed soft graded soil / sand in place of available excavated material and / or other suitable soil as per applicable standards / specifications, including backfilling of excavated trench for specified length after laying and padding of pipeline, including transportation of such special backfill material over all distances, complete. | Item45 | 900 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
46 | CROSSING OF STEEL PIPELINE BY OPEN CUT | Item46
47 | Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insatllation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed. | Item47
48 | Road Crossing By Open Cut Method Road Crossings at various locations by Open cut Method along with laying of MDPE upto 180 mm Dia if necessary as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item48
49 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item49 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
50 | Line pipe detail 6" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item50 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
51 | Line pipe detail 4" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item51 | 60 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
52 | Water body Crossing By Open Cut Method water/ canal/ nallah/ drain/ channel Crossings at various locations by Open cut Method along with laying of MDPE upto 180 mm Dia if necessary as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item52
53 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item53 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
54 | Line pipe detail 6" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item54 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
55 | Line pipe detail 4" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item55 | 60 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
56 | Note: Laying of the pipeline by the approved method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item56
57 | Backfilling of the Road/water/ canal/ nallah/ drain/ channel Crossings/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority. | Item57
58 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item58
59 | CROSSINGS/LAYING ALONG THE ROAD BY HDD METHOD | Item59
60 | Complete work of the any crossing (between the limits are defined as approved drawings) by HDD method including "Receiving and taking over" owner supplied three layer PE coated line pipes from Owner's designated place to issue/ dump site(s) and transportation to Contractor's stock yard/ work shop/ work site including all handling loading, unloading, aligning etc. supply of all Contractor supplied material, manpower, equipment, other resources and aquiring the required land for storage, fabrication inclduing string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type Heat Shrink Sleeve and repair of pipeline coating with special repair patch materials as per specification,pre-testing etc. of complete string made for crossing access for Contractor etc and execution of, but not limited to, following works in accordance with specifications scope of work and instructions of Engineer-in-charge and as per all provision of Contract Document. | Item60
61 | Pre-construction surveys based on site visit, collection of historical data from irrigation/ concerned department including design & calculation and detail engineering and making of crossing drawing for getting their approval from concerned Authority/ Engineer-in-charge, getting work permit/ NOC for water crossings/ road crossings as well as utility crossings (if any) encountered during crossing prior to start the execution of work. | Item61
62 | Directional drilling to required depth from top of road including maintenance of drill hole in all types of strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) at all depth to accommodate the pipeline at all conditions encountered during rail/ road crossing by approved HDD methods for providing minimum cover specified in code/ specification or the actual depth as decided by concerned authority, whichever is more. | Item62
63 | In case of water crossing, drilling to the required depth on the banks and bed including maintenance of drill hole in all types of soil strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) all depth to accommodate the pipeline a by HDD methods for providing with minimum cover over top of the pipe at all point across the maximum possible width of water bed (as per drawing) either 1.5 mtrs. below the predicted scour profile expected during the life time of the pipeline or 2.5 mtrs. below the available lowest firm bed (if scour profile/ depth not available) of the water crossing by ascertaining bed level upto 50 mtrs. both the side from crossing location or the actual depth as decided by concerned Authority/ Engineer-in-charge whichever is more. | Item63
64 | Laying of the pipeline by the approved HDD method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints with special type Dirax Heat Shrink Sleeve or equivalent and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item64
65 | Backfilling of the ditch/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority and all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specification, approved drawings, calculations, methods and to the satisfaction of Engineer-in-charge and/or as directed by concerned Authority. | Item65
66 | Post installation hydrotest dewatering and tie-in with pipeline at either side of crossing/banks etc. | Item66
67 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item67
68 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 (along with laying of 4'' Steel Pipe for MDPE if necessary) by HDD Method . | Item68 | 120 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
69 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 150 mm NB x 6.4 mm thk. of API X-52 (along with laying of 4" Steel Pipe for MDPE if necessary) by HDD Method. | Item69 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
70 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 100 mm NB x 6.4 mm thk. of API X-52 (along with laying of 4" Steel Pipe for MDPE if necessary) by HDD Method. | Item70 | 60 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
71 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item71 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
72 | Laying along the Road by carrier pipeline of size 150 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item72 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
73 | Laying along the Road by carrier pipeline of size 100 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item73 | 60 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
74 | Installation of carrier pipes by rock drilling for Road/water/Canal/ nallah/ drain/ channel/along the road, or wherever required in all types of hard rock. It includes survey of the underground utilities, submission of profile for approval, execution of the work as per the standard procedure, including , excavation of the pits, insertion/pulling of the carrier pipe, removal of malba, subsequent backfilling and restoration of the facility crossed as per original condition, including supply of all other materials, equipment, consumables, manpower etc including string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type of Heat Shrink Sleeve (Direx) and repair of pipeline coating with special repair patch materials as per Specification, pre-testing etc. of complete string made for crossing/ laying access for Contractor etc. and execution of, but not limited to, following works in accordance with specifications and instruction of Engineer-in-Charge and as per all provision of Contract Document. Balance activities as defined in SOR Item of open trench. Note:The length of HDD mentioned is tentative and may vary to the considerable extent depending upon requirements as per site conditions. The length mentioned in SOR is indicative for all the crossing to be done by HDD, numbers and locations shall be decided by Engineer-in-Charge depending upon site condition. Payment for the length of final tie-in carrier pipeline string with mainline laid by HDD are inclusive in this above item rate. No separate payment shall be made under other clauses mentioned elsewhere. Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item74
75 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 (along with laying of 4'' Steel Pipe for MDPE if necessary) by HDD Method . | Item75 | 110 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
76 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 150 mm NB x 6.4 mm thk. of API X-52 (along with laying of 4" Steel Pipe for MDPE if necessary) by HDD Method. | Item76 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
77 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 100 mm NB x 6.4 mm thk. of API X-52 (along with laying of 4" Steel Pipe for MDPE if necessary) by HDD Method. | Item77 | 60 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
78 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item78 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
79 | Laying along the Road by carrier pipeline of size 150 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item79 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
80 | Laying along the Road by carrier pipeline of size 100 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item80 | 60 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
81 | Note: (i) Crossing width & Actual string length for HDD shall vary as per design calculations & site condition so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. | Item81
82 | (ii)Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item82
83 | (iii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by HDD method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item83
84 | (iv) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossing at different locations. | Item84
85 | (v) The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. | Item85
86 | Note: (i) Quantity mentioned under item nos. 48, 52 are indicative only for different location of roads/water/ canal/ nallah/ drain/ channel Crossings. (ii) Actual length & width of individual crossing and cover from top of casing pipe/ carrier pipe string may vary depending upon site condition, approved crossing drawings, specifications etc. and / or as decided by Engineer-in-charge/ Concerned Authority. | Item86
87 | (iii) Payment for supply & installation of Zinc ribbon anode and its design excluded from above item and covered elsewhere in the SOR. (iv) Payment for the length carrier pipeline string inserted in casing pipe laid by Boring are covered separately and shall be paid under other clauses mentioned elesewhere in the SOR. | Item87
88 | Excavation beyond 1.5m depth in case of crossing of utilities/ drain/ culverts etc. through open cut upto the following depth (including restoration of the damaged area to its original condition and satisfaction of the Engineer-in-charge / concerned authorities) : - | Item88
89 | In all type of surface (Kachha/ built-up surface / Hard surface) of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. The other activities are as per SOR 1.1. Payment for cutting of hard rock, if any, is covered unders SOR no. 96 | Item89
90 | Deeper than 1.5 m & upto 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item90 | 500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
91 | Deeper than 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item91 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
92 | Deeper than 1.5 m & upto 2.5 m below existing level (for 150 (approx.) mm NB Pipeline) | Item92 | 60 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
93 | Deeper than 2.5 m below existing level (for 150 (approx.) mm NB Pipeline) | Item93 | 60 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
94 | Deeper than 1.5 m & upto 2.5 m below existing level (for 100 (approx.) mm NB Pipeline) | Item94 | 300 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
95 | Deeper than 2.5 m below existing level (for 100 (approx.) mm NB Pipeline) | Item95 | 150 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
96 | Excavation of hard rock | Item96
97 | Excavation of hard rock wherever hard rock of single piece exceeding 1.0 m in length removable by pneumatic chisel/ drill as per direction of EIC. | Item97 | 3500 | Cub. M |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
98 | REPAIR OF COATING DEFECTS (NOT ATTRIBUTED TO CONTRACTOR) | Item98
99 | Repair of Holiday in Coating (Noted and recorded at the time of "receiving and taking over") Supply of all coating repair materials as per requirements of specification to be compatible with line pipe coating material, supply of all consumables, utilities, equipments and all manpower required, pipe cleaning and surface preparation, repairing of coating defects (resulting in holiday) and testing including all handling, transportation, etc. for line pipes, performing all works necessary for the completion of the works stirctly in accordance with relevant specification and instructions of Engineer-In-Charge. This rate shall be applicable per sq. cm of the exposed steel area exposed steel area. | Item99 | 2200 | Sq. cm. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
100 | PERMANENT MARKERS Supply, fabrication and installation of all types of permanent markers along the route including all associated civil works such as excavation in all types of soil, construction in all types of soil, construction of pedestals and grouting with concrete, clearing, supply and application of approved colour and quality of primer and paint, stencil letter cutting for numbers, direction, change etc., restoration of area to original condition and performing all works as per drawing, specification and instruction of engineer-in-charge. | Item100
101 | Pipeline RCC boundary / route marker as per drawing | Item101 | 120 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
102 | Pipeline warning markers with post & foundations | Item102 | 40 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
103 | Pipeline direction marker with post & foundations | Item103 | 25 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
104 | Pipeline KM with post & foundations | Item104 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
105 | HOOK -UP | Item105
106 | Hook-up of proposed pipeline by welding of final tie-in-joint with any existing laid pipeline portion of river X-ing ,existing Tap-off & battery limit of section IV including Hook-up point of the existing pipeline to be made ready for welding by cutting of flanges / valves / headers at all depth in all type of soil etc. Venting of N2 / gas / gas mixture as required purging of N2 Gas (if required), rebevelling as required, radiography and other NDT examination, joint coating as per specification.Contractor shall supply of all consumables, manpower, machinaries, materials, N2 gas etc. and carry out all works as per the provisions of Contract document and instructions of Engineer-in-charge. | Item106
107 | For 12" NB | Item107 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
108 | For 6" NB | Item108 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
109 | For 4" NB | Item109 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
110 | PRE-COMMISSIONING AND ASSISTANCE IN COMMISSIONING OF PIPELINE SYSTEM Swabbing, drying, purging with nitrogen of the complete pipeline network and the associated facilities being installed to the specified acceptance criteria, carrying out pre-commissioning works, providing assistance during the complete duration of commissioning operations for entire pipeline network system including supply of all equipment, man-power, consumables (including pigs & nitrogen required for purging with maintaining nitrogen column of mininum 10% of pipeline geometric volume) materials for all temporary works and performing all associated works, complete as per the relevant specifications, other provisions of Contract document and instructions of Engineer-in-charge. | Item110
111 | For 12" NB Pipeline | Item111 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
112 | For 6" NB Pipeline | Item112 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
113 | For 4" NB Pipeline | Item113 | 1000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
114 | IDLE TIME PRESERVATION OF PIPELINE Preservation of complete pipeline and associated facilities forming part of the pipeline as per Bid document and its maintenance including supply of all consumables, all equipment, manpower, etc. complete as per the requirements of specifications, other provisions of Contract document and instructions of Engineer-in-charge. Note : Owner reserves the right to exercise either or none of the rates below. | Item114
115 | By filling and pressurizing with nitrogen to a pressure of 2 bar(g) for a period of 3 months. | Item115
116 | For 12" NB Pipeline | Item116 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
117 | For 6" NB Pipeline | Item117 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
118 | For 4" NB Pipeline | Item118 | 1000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
119 | For every additional period of one month or part thereof | Item119
120 | For 12" NB Pipeline | Item120 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
121 | For 6" NB Pipeline | Item121 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
122 | For 4" NB Pipeline | Item122 | 1000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
123 | RCC VALVE PITS All civil works including supply of all materials, excavation of pit, piping supports including all PCC and RCC works for valves pits including pedestals with insert plates as required sealing of pipe at valve pits, providing cover etc. and finishing , clean-up and restoration of site, filling and grading of area around valve station for avoiding any local flooding of area, as per typical drawing and specification enclosed and instructions of Engineer-in-charge. In this item, instead of Brick Work, RCC will be done | Item123
124 | Valve Pit of Size 2m x 2m | Item124 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
125 | Valve Pit of Size 1.5m x 1 m | Item125 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
126 | Valve Pit of Size 1 m x 1 m | Item126 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
127 | SUPPLY OF ASSORTED PIPE, FITTINGS AND FLANGES Complete works of supply of pipes, flanges & fittings for aboveground & underground installation including all taxes, duties, transportation and inspection charges but not limited to, the following items in accordance with PMS (piping material specification), relevant specifications & drawings indicated in job specification under SCC (technical) and instructions of Engineer-in-charge and as per all provisions of the CONTRACT DOCUMENT. - Handling including lifting, transportation from Contractor Stores to CONTRACTOR's workshop for fabrication and/ or to work site for field fabrication and erection for all piping items supplied by Contractor. | Item127
128 | Carbon Steel Pipe (A 106, Seamless B-36.10/ API X 52 ) | Item128
129 | Size Rating/ Schedule | Item129
130 | 2" NB, BE Sch. 80 | Item130 | 50 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
131 | 1" NB, PE Sch. 80 | Item131 | 32 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
132 | ¾" NB, PE Sch. 160 | Item132 | 28 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
133 | Flanges | Item133
134 | Weld Neck (B-16.5, 300# A105,125 AARH, Serrated finish) | Item134
135 | Size Rating/ Schedule | Item135
136 | 6" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item136 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
137 | 4" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item137 | 5 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
138 | 2" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item138 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
139 | 3/4" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item139 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
140 | Blind Flanges (B-16.5, 300# A105,125 AARH Serrated) | Item140
141 | Size | Item141
142 | 6" NB, RF | Item142 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
143 | 4" NB, RF | Item143 | 5 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
144 | 2" NB, RF | Item144 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
145 | 3/4" NB, RF | Item145 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
146 | Elbow (Seamless) | Item146
147 | 90° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item147
148 | Size Rating/ Schedule | Item148
149 | 12" NB 300# | Item149 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
150 | 6" NB 300# | Item150 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
151 | 4" NB 300# | Item151 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
152 | 2" NB Sch. 80 | Item152 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
153 | 45° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item153
154 | Size Rating/ Schedule | Item154
155 | 12" NB 300# | Item155 | 22 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
156 | 6" NB 300# | Item156 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
157 | 4" NB 300# | Item157 | 10 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
158 | 2" NB Sch. 80 | Item158 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
159 | 90° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item159
160 | Size Rating/ Schedule | Item160
161 | 12" NB 300# | Item161 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
162 | 6" NB 300# | Item162 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
163 | 4" NB 300# | Item163 | 10 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
164 | 45° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item164
165 | Size Rating/ Schedule | Item165
166 | 12" NB 300# | Item166 | 22 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
167 | 6" NB 300# | Item167 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
168 | 4" NB 300# | Item168 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
169 | 22½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D) Min Thickness 6.4mm | Item169
170 | Size Rating/ Schedule | Item170
171 | 12" NB Sch. Std. | Item171 | 16 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
172 | 6" NB End thickness to match with pipe wall thickness | Item172 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
173 | 11½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D), Min Thickness 6.4mm | Item173
174 | Size Rating/ Schedule | Item174
175 | 12" NB 300# | Item175 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
176 | 6" NB 300# | Item176 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
177 | Tees (Seamless) | Item177
178 | Equal Tee (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item178
179 | Size Rating/ Schedule | Item179
180 | 12" NB x 12" NB x 12" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item180 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
181 | 6" NB x 6" NB x 6" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item181 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
182 | 4" NB x 4" NB x 4" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item182 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
183 | 2" NB x 2" NB x 2" NB Sch. XS | Item183 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
184 | Unequal Tee (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item184
185 | Size Rating/ Schedule | Item185
186 | 12" NB x 12" NB x 6" NB Sch. Std. x Sch. Std. | Item186 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
187 | 12" NB x 12" NB x 4" NB Sch. Std. x Sch. Std. | Item187 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
188 | 4" NB x 4" NB x 2" NB Sch. 80 x Sch.80 | Item188 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
189 | 6" NB x 6" NB x 4" NB Sch. Std.x Sch. XS | Item189 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
190 | Reducer (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item190
191 | 12" NB x 6" NB Min Thickness 6.4mm | Item191 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
192 | 12" NB x 4" NB Min Thickness 6.4mm | Item192 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
193 | 6" NB X 4" NB Min Thickness 6.4mm | Item193 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
194 | 4" NB X 2" NB Min Thickness 6.4mm | Item194 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
195 | Weldolet and Sockolet | Item195
196 | Weldolet (MOC A105 & DIM. MSS SP 97) | Item196
197 | Size Rating/ Schedule | Item197
198 | 12" NB x 2" NB Sch. 80. | Item198 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
199 | 6" NB x 2" NB Sch.80 | Item199 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
200 | 4" NB x 2" NB Sch. 80 | Item200 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
201 | Sockolet (MOC A105 & DIM. MSS SP 97) | Item201
202 | 12" NB x 3/4" NB #6000 | Item202 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
203 | 6" NB x 3/4" NB #3000 | Item203 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
204 | 6" NB x 1" NB #3000 | Item204 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
205 | 4" NB x 3/4" NB #3000 | Item205 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
206 | Butt Weld Disc End Cap (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item206
207 | Size Rating/ Schedule | Item207
208 | 12" Sch. Std. | Item208 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
209 | 6" Sch. 40 | Item209 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
210 | 4" Sch. 80 | Item210 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
211 | Fabrication & Installation of Underground Valve Assembly | Item211
212 | 12"NB Isolation Valve/tap-off assembly as per Drg. No. MNGL/Plng./Steel/40 | Item212 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
213 | 6" NB Isolation Valve/tap-off assembly as per Drg. No.MNGL/Plng./Steel/40 | Item213 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
214 | 4" NB Isolation Valve/tap-off assembly as per Drg. No. MNGL/Plng./Steel/40 | Item214 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
215 | Note: | Item215
216 | For all the supply items mentioned above, procurement shall be made as per enclosed Data Sheets and respective technical specification, after due approval of Engineer-in-charge. | Item216
217 | The quantities mentioned above are tentative and quantities for above supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item217
218 | PLANT PIPING (ABOVEGROUND) Fabrication and testing of carbon steel piping and fittings, valves, IJ, including supply of all consumables, equipment, manpower, and other resources and execution of job as per instruction AIC/EIC.Transportation of all piping items from Owner's and/ or Contractor's storage point to work at site/ workshop as applicable, complete work of fabrication, erection, painting, testing of pipes, flanges and fittings and making ready for further Commissioning / Start-up of carbon steel piping of all sizes and ratings including supply of all consumables, equipment, manpower and other resources and execution of, but not limited to, as per all provisions of the CONTRACT DOCUMENT. | Item218
219 | Fabrication including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site, cutting, edge preparation, inclusive of grinding the edges of pipes, fittings, flanges, reducers etc. to match with the matching edges of uneven thickness, wherever required, fit-up, welding of pipes and fittings like elbows, tees, reducers, weldolets, sockolets, Valves, IJ etc. flanges, vent and drain point connection, Radiography and NDT of all joints etc, including providing stubin connections, fabricated fittings and reinforcement pads etc., as required. | Item219
220 | Erection of pipes of all types and thickness at all elevations, connecting with equipment nozzle, aligning, installation and carrying out connected activities for all types of valves, all online instruments and fittings of all sizes of elbow, reducers, tees, flanges, blind flanges, spectacle blind flanges, branch connection / tapping for pressure gauges, including installation of gaskets and bolts. | Item220
221 | Erection including prior cleaning, lifting, placing on pipe sleepers and supports, overhead on racks, skids and at all elevations including installation and carrying out connected activities for all types of valves including supply and fixing of gaskets, studs/ bolts, nuts wherever required for all sizes, levelling, aligning, joining of flanges, blind flanges, connecting with equipment, nozzles, strainers, tie-in with existing piping/facilities, etc. tapping for inline instruments like pressure gauges, thermowells, sample connection, etc. | Item221
222 | Hydro testing of the piping job shall be conducted at pressure mentioned in specification for a period of 4 hours by using de-mineralised water, to check its strength. No visible leakages shall be detected during the test. Testing shall be conducted as per tender specification. | Item222
223 | Preparation of final bill of material based on piping GADs. | Item223
224 | Preparation of isometric and fabrication drawings. | Item224
225 | Carrying out Non-destructive testing as required except items mentioned in sl. no. 286 of SOR. | Item225
226 | Painting of entire system (including aboveground all pipes fittings, flanges and accessories) as per specifications suitable for highly corrosive area environment including supply of approved paints and primers, application of primer and paints, indentification lettering/ numbering, colour coding, etc. as specified including rub down & touch up of shop primer or scrapping of shop primer wherever required by COMPANY and providing scaffolding for all heights etc. | Item226
227 | Cleaning and flushing by water/ compressed air, testing of the systems including hydrostatic, pneumatic and any other type of testing as specified, draining, drying by compressed air/other methods approved by COMPANY. | Item227
228 | Precommissioning & making operational all piping system and equipments. | Item228
229 | Commissioning Contractor scope shall provide all necessary assistance in term of supply of man-power, equipment, tools and tackles required amount of nitrogen for purging of entire terminal piping system including equipments etc. to the company during commissioning activities. | Item229
230 | Completion of all such work in all respects as per scope of work and as per drawings, specifications and instructions of the COMPANY and keeping the system ready in all respects for further commissioning and start up. | Item230
231 | Hook-up works (with client/ consumer piping at battery limits): | Item231
232 | Complete Carbon Steel aboveground Piping Work with painting including all fittings, flanges and supply of all required gaskets, studs bolts & nuts etc. and Any other work and material required for the completion of the work and not covered above and desired by EIC shall be in the scope of contractor | Item232
233 | Carbon Steel Pipe (ASTM A 106, Seamless B-36.10 / API X 52) | Item233 | 200 | inch Dia |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
234 | 1) Pipe Specification and thickness may vary depending upon availability of pipe. No extra payment shall be made for this. 2) All butt welded fittings & flanges end shall generally match with connecting pipe wall thickness. However, in case of misalignment, Contractor shall have to do end preparation without any extra cost. 3) All o-lets less than 2" NB size, all sizes of coupling and nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under erection rate. | Item234
235 | Aboveground installation of Insulating Joint & Valves etc. Handling including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site and installation of all types of valves, insulating joint including assembly of valve accessories, (if any) by bolting, threading or welding, supply and insertion of gaskets, nuts & bolts, nipples, etc. at all elevations of pipe sleepers, supports or overhead on racks, equipments nozzle, skid & painting etc. supply of all consumables, manpower, equipment, etc. for completion of all works as per scope of work and as per drawings, specifications and instructions of Engineer-in-charge including servicing/ cleaning of valve wherever requried. | Item235
236 | Welded Valves (Full Bore/ Reduced Bore) Ball / Globe / Check Valve | Item236
237 | Size Rating/ Schedule | Item237
238 | 4" NB 300# | Item238 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
239 | 2" NB 300# | Item239 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
240 | Sockolet Welded Valve (Ball / Globe Valve) | Item240
241 | Size Rating/ Schedule | Item241
242 | 1" NB 800# | Item242 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
243 | ¾" NB 800# | Item243 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
244 | 12" NB, 300# - Insulating Joints | Item244 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
245 | 6" NB, 300# - Insulating Joints | Item245 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
246 | 4" NB, 300# - Insulating Joints | Item246 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
247 | STRUCTURAL WORKS | Item247
248 | Supply of erection of single leaf mild steel gate 2.5m high with mesh upto 2m height and barbed wire fencing and 2m wide complete in all respect including painting as per TS on all MS items, all works as per specification and drawings excluding foundations and RCC beams. | Item248 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
249 | Supply of all materials, fabrication and erection of chain link fencing 2.5m high with mesh up to 2m height and barbed wire fenching complete in all respects including painting as per TS on all MS items, all works as per specification and drawings excluding foundation and RCC beams. | Item249 | 150 | RM |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
250 | Pipe Supports & Other Structures | Item250
251 | Supply, fabrication and erection of all types of pipe supports like clamps, saddle, guide stops, cradles, turn buckles, anchors, T-posts; stockade/ trestle and pipe bridge for overhead piping; frames for canopy, approach ladders and platforms, crossover, cable tray supports, etc. including painting suitable for highly corrosive area as per specification labour and supervision & complete work as per drawings, specifications and instruction of Engineerqw-incharge. (Bolts, nuts, washers, U-clamps etc. for supporting shall be supplied by the Contractor within the rates quoted. These items will not be measured and paid seperately). The work is to be completed in all respect as per scope of work and specification. | Item251 | 300 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
252 | Notes: | Item252
253 | The quantities indicated are estimated values and hence are approximate. Final payment will be made based on actual quantities to be certified by the Purchaser. | Item253
254 | The cost of MS bolts (permanent and service(, washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants etc., as required for the work shall be deemed to be included in the quoted rates. | Item254
255 | All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accrodance with time schedule, are deemed be included in the quoted rates. | Item255
256 | CIVIL WORKS | Item256
257 | Site Grading Excavation in earth and filling to the grades and levels shown in the approved drawings in all kinds of conditions including for Road embarkments, using approved quality good earth from designated borrow area, for all heights and depths including clearing and stripping (min. 150mm) of the area marked for filling, taking spot levels, consolidating the exposed natural soil surface, excavating the earth from borrow area loading, transporting & unloading, spreading in layers not exceeding 150mm thickness, breaking clods, watering (if reqd.), ramming and compacting by manual/ mechanical means to give minimum 92% of modified Proctor's density of earth, testing & dressing including disposal of all unserviceable material all complete as per specifications and directions of Engineer-in-charge. | Item257 | 150 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
258 | (Rate to include cost of all labour, tools, tackles, equipment, hire charges, cost of borrow earth by way of royalties, right of way, cess etc., as applicable with all bye works and sundry works). | Item258
259 | Plain Cement Concrete Supplying and laying plain cement concrete (including shuttering of required) in all types of concrete works including levelling courses below foundation, substructure, superstrcuture, chambers, cable tranch, under floors and any other locations, at all leveies as per drawings, specifications and directions of the Engineer-in-charge. | Item259
260 | PCC 1:2:4 1 Cement : 2 Coarse sand : 4 stone aggregate 20mm nominal size. | Item260 | 400 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
261 | Reinforced Cement Concrete Providing and laying reinforced cement of grade M-20 with 20mm and down grade crushed stone aggregate in all types of structures like foundations, pedestals, pedestal bases, pipe supports, sleepers cable trench inlcuding constrcution joints, bitumen painting on surface in contact with soil, providing and fixing reinforcing steel, shuttering, inserts, finishes etc. at all depths and heights complete as per drawings, specifications and direction of the Engineer-incharge. | Item261 | 300 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
262 | Rate to include cost of all labour, tools, tackles, equipment, hire charges, supply of all maerials such as minimum 43 grade cement including sulphate resistant cement for substructures, R/F steel, Inserts, bolts, conduits, bitumen, other minor constrcution materials, shuttering, stanging, earthwork in excavation and backfilling using serviceable earth in all conditions, shorting bailing and pumping out water, testing of concrete, curing etc. with all bye works and syndry works. | Item262
263 | TEMPORARY CATHODIC PROTECTION SYSTEM | Item263
264 | Design, detailed engineering, supply, installation, testing and commissioning of the temporary Cathodic protection system using Mg/ Zn galvanic anodes to protect the external surface of 3 LPE coated entire 5.5 km (approx.) long steel pipeline network against corrosion for design life of minimum 1 year or till commissioning of PCP system whichever is later as per standard specification No. MNGL/Steel/TS/15 for temporary cathodic protection system. Scope shall also include but not limited to the following for completion of jobs: | Item264
265 | Measurement of soil resistivity along the right of way of the main pipeline route as per specification for design & installation of anodes. | Item265
266 | Collection of additional data related to cathodic protection along the right of way of pipeline as per specifications. | Item266
267 | Supply, installation, testing & commissioning of one set of spark gap arrestor with 2 plate Zinc grounding cell of 20 kg net weight each across each insulating joint as per specification. | Item267
268 | Supply, installation, testing & commissioning one set of polarisation cell with zinc anode at all high tension (66KV or higher) electrical power transmission line/Equipment crossing or running parallel to the pipeline for grounding purpose as per specification. The rating shall depend upon anticipated fault current & ground bed resistance at the location of installation. However, the rating of polarisation cell (krick) shall not be less than 5 KA & number of 20 kg net weight zinc anode shall not be less than two. | Item268
269 | Supply & installation of Zinc Ribbon Anodes at 4-8 O’Clock position in the interval of 2 metre (max.) on carrier pipes at all cased crossings i.e. railways/ roads etc. | Item269
270 | Monitoring of the protection system for 6 months. | Item270
271 | All civil/ structural works related to TCP system including supply of bricks, cement & steel etc. required for completion of the system. | Item271
272 | For 12" | Item272 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
273 | For 6" | Item273 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
274 | For 4" | Item274 | 1000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
275 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item275
276 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item276
277 | FIELD INSTRUMENTATION | Item277
278 | PRESSURE INSTRUMENTS | Item278
279 | Supply , Installation of Pressure Gagues and their accessories inclusive of supply of necessary piping materials and tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/ manifolds & hydraulic testing (exclusive of calibration of instruments) as per installation standard attached elsewhere in Tender Document and Supply as per Data Sheet No.MEC/23K8/05/E5/I/001/DS-PG. Give breakup of supply and Installation rate. | Item279 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
280 | CALIBRATION | Item280
281 | Calibration of the instruments listed below including removal of instruments from pre-installed locations like panels, enclosure racks, fields etc. and refixing them back in respective/ required places, providing equipments, necessary test jigs, instrument air and all consumables. Calibration reports shall be prepared and to be submitted to the Purchaser/ Consultant. | Item281
282 | Pressure Gauges | Item282 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
283 | Note: | Item283
284 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item284
285 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item285
286 | Laying of MDPE pipe along with Steel pipe line Excluding supply of all MDPE pipe (PE 80/100,SDR11), but Including supply of Bends, Couplers, End caps, Tees, PE Reducer, CS to PE Fitting, Saddle Tapping, Warming mat, etc. as required to complete the job. ( Particular job specification.) "Receiving and taking-over" as defined in the specification, handling, loading, transportation and unloading of Owner supplied MDPE line pipes (PE80/100, SDR11) of all sizes (as free issue items) from Owner's designated place(s) of issue to Contractor's own stock-yard(s)/ Work Shop(s)/ work-site(s) including proper storing, stacking, identification, providing security & insurance cover , including supply of accessories of all sizes & thickness like Bends, Couplers, End caps, Tee, PE Reducer, CS to PE Fittings, Saddle Tapping, Warning Mat, etc.. | Item286
287 | Stringing/ uncoiling of the MDPE line pipe on the pipeline Right-of-Use, laying/ installation of MDPE line pipe alongwith steel pipeline (alongwith installation of required accessories as mentioned above) of following sizes, including executing all works; fabrication, access for construction; supply of all materials (except Owner supplied materials), consumables, labour and other incidental works and handing over the same after return of the surplus pipes to the Owner's designated stockyard(s); carrying out all temporary, ancillary, auxiliary works required to make the MDPE pipeline ready for commissioning as per drawings, specifications, scope of work indicated in PJS and other provisions of Contract document and instructions of Engineer-in-charge. | Item287
288 | UP to Dia 90mm | Item288 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
289 | Dia 125mm | Item289 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
290 | Note : The quantities indicated above against all individual item are tentative and may vary considerably depending upon site condition, methodology adopted as per site requirement with due approval of Owner/ Consultants. | Item290
291 | PIPING WORKS FOR SECTIONALISING VALVE STATION-CUM-TAP-OFF POINT All works for fabriaction and installation of all piping above ground at all elevations and below ground at all depth for Sectionalising Valve Station alongwith preparation of construction drawings duly approved by EIC, in all type of terrains and soils including transportation and handling of all Owner supplied materials i.e. extended stem butt welded sectionalising gas actuated ball valve, other types of valves, line pipes for mainline, 4" NB pipe for all branch line including ventlines from Owner's designated place(s) of issue to work site. | Item291
292 | Contractor shall supply all required size & type of piping material like pipes, fittings & flanges etc. as per PMS alongwith 2" NB pipe for all branch line & vent line (wherever required) including supply of all consumables, manpower, machinaries, materials etc. and carrying out all mechanical works of underground and above ground piping including fabrication, welding, nondestructive testing of welds, weld repairs/ retesting, cleaning/ flushing, pre-hydrotesting & hydrostatic testing, dewatering, functional testing, cutting of mainline and bevelling (if required) | Item292
293 | assembly, including radiography of tie-in joints, corrosion, coating and external painting as required, installation of instruments like pressure/ temperature instruments/ gauges alongwith complete SS Tubing works including supply of SS Tube and thier accessories etc., as required, obtaining all statutory clearances, approvals and permissions for the works (wherever required), making of valve pit (for detail refer relevant drawings) for SV Stationscum- tap-off points enclosed with tender filled with sand, excavation and filling in all types of soils including soft/ hard rock for installation of piping/ pipe supports providing pipe supports, area fencing and gate including all associated civil and structural works; painting, finishing, clean-up and restoration of site; preparation of as-built drawings, documents and project records and performing all works as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge. In this item, instead of Brick Work RCC will be done | Item293
294 | Type - I SV Station on 12" Pipeline | Item294 | 1 | Lumpsum for each |  |  |  | Excess(+) | 1 | Full Conversion | INR |  | 18% | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
295 | Note: i) Work under above items are exclusive of all works associated with main pipeline covered under Item No. 1.0 above. ii) All civil/ structural works including area fencing and gate, valve pits except for piping support will be paid separately as per unit rate provided elsewhere in the SOR. iii) All coupling, nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under above item rate. | Item295
Total in Figures | [51 empty] | 0 | 0 | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## BoQ6 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR | [49 empty] | 1
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Maharastra Natural Gas Ltd.,Pune
Name of Work: TENDER FOR LAYING & CONSTRUCTION OF 12” NB X 6 KM , 6" NB X 0.2 KM & 4" NB X 1.5 KM U/G STEEL PIPELINE NETWORK & ASSOCIATED WORKS FROM NEAR BHIWAPUR VILLAGE ROAD, BHIWAPUR TO NEAR RAIGAON BRIDGE, RAIGAON & SURROUNDING AREAS IN NANDED GA (Section No-06)
Tender No: MNGL/CP/2024-25/109
Do you want to quote for this sheet ? |  |  | Yes
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE / SCHEDULE OF RATES (SOR) (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Rate inclusive of all taxes and duties except Goods & Service Tax (Rs.) | Per Unit Goods & Service Tax (GST) In % (To be entered by the Bidder) | GST in Rs. | Unit rate inclusive of all taxes & duties including GST (Rs.) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | CARBON STEEL PIPES | Item1
2 | PIPELINE LAYING / INSTALLATION in all type of surface (Normal/built-up surface) "Receiving and taking over" as defined in the specifications, handing, loading, transportation and unloading of Owner supplied 3-Layer PE coated linepipes from Owner's designated stack-yard to Contractor's stock yard/workshop/work-site including preliminary activities, preparation of drawings, wherever required for crossing etc. including handling, stacking, stringing on the pipeline Right-of-Use/ pipeline route alignment, carrying out inspection of company supplied materials including linepipes at the time of taking over, laying/ installation of coated linepipes, associated burried valves, barred tees, insulating joints, flanges & fittings of all sizes, thickness & ANSI class rating and accessories as per specification wherever required depending on site condition including execution of all works, "taking over", handling , including loading and unloading, transportation of Owner supplied materials other than linepipe from Owner's designated place (s) of issue to work site, | Item2
3 | additional lands required for Contractor's storage, fabrication, access for construction, procurement and supply of all materials (except Owner supplied materials), consumables, equipment, labour and other inputs, carrying out all temporary, ancillary, auxiliary works, aquistion of ROU/ROW for laying of pipeline from HDD Exit and entry point to Tie in Point of existing Pipeline/ ROU, ready for commissioning of pipeline as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge, including but not limited to carrying out the following works: | Item3
4 | Surveying of route and detours required at the time of execution including marking the same in topographical sheet, preparation of construction drawings showing survey details, and submit same to Owner for review / approval. | Item4
5 | Staking and installation of construction markers, clearing, fencing, grubbing, cutting of trees, full filling all the requirements of various statutory/ environment authorities to the entire satisfaction of concerned authorities, grading of work area. Shifting of all obstruction within the ROU/ Pipeline route alignment viz. electrical lines/ poles, telephone line / poles, etc. coordination with concerned authorities and obtain permissions from these authorities. | Item5
6 | Trenching to all depths by excavation in all types of soils including soft/ hard rock and different type of pavement / footpath / roads etc. including rock breaking, chiselling or otherwise cutting etc. as required and storing excavated soil, reusable materials at designated area as directed by Engineer in charge and to a width to accommodate the Steel pipeline and MDPE as per the relevant standard/ specification etc. [The minimum depth of the top of pipeline shall be 1.2m measured from top of pipeline coating to the top of undisturbed surface of the soil or as per SCC/ OISD - 141 / 226, whichever is higher]. Dewater of trenches if required as per site condition. | Item6
7 | Carrying out repairs of pipe defects/ replacement in case of irreparable defects and repairs of defects of pipe coating not attributable to Owner including defects/ damages occurring during transportation / handling. | Item7
8 | Stringing of line pipes along pipeline trench / ROU on straw / sand / soft soil bags including supply of bags and its filling materials. | Item8
9 | Checking, cleaning, aligning, bending, cutting and bevelling (as required) of pipes for welding and field adjustments including pipe fittings, welding, carrying out non-destructive testing of welds as required including 100% radiography by X-ray and providing all requisite equipment, labour, supervision, materials, films, consumables, all facilities and personnel to process, develop, examine and interpret radiographs and other tests as required, carrying out repairs of weld joints found defective by Engineer-in-Charge, carrying out re-radiography and other tests as required on repaired joints. | Item9
10 | Carrying out installation of carrier line pipe at all minor crossing viz. carttrack, pathway, water bodies etc. at designated depth by open cut (except at crossing by HDD method). | Item10
11 | Carrying out installation of carrier line pipe in the casing pipe at cased crossing (excluding installation of casing pipes which is covered separately). | Item11
12 | Coating of field weld joints, long radius bends (R=3D), elbows, buried fittings and valves etc. including supply of coating materials etc. (i.e. heat shrinkable sleeves and high build epoxy etc.) as per PJS & Technical Specification compatible with 3 layer PE coating material of the line pipe. | Item12
13 | Counting the number and type of trees cut in presence of DFO/concerned authorities and keeping record thereof, stacking and handing over of all cut tress. | Item13
14 | Installation / lowering the pipeline in trench to required depth as per PJS, Techanical Specification & drawings, supply & placement of 1.0mm thk. HDPE Yellow colour warning mat,RCC tiles (300 mm width x 50 mm thick) over the pipeline & MDPE Pipe in same trench along the complete route as per standard drawings, data sheets & technical specifications, padding around pipeline as per Standard Drg. no. MNGL/Plng./Steel/03 with suitable soil duly approved by EIC including supply of padding material, backfilling and its compaction to the satisfaction of concerned authorities with excavated earth / borrowed select soil including supply of borrowed select soil duly approved by EIC before backfilling and make ready for restoration to be done by Onwer / concerned authorities. | Item14
15 | Supply and installation of slope breakers, wherever required or, as directed by Onwer / Engineer–in–charge. | Item15
16 | Crossing the all-foreign pipeline / HT line / cable / any other utilities etc. with necessary concrete / HDPE sheet protection including coordination with all agencies and obtaining NOC | Item16
17 | Supply and installation of bank protection alongwith backfill materials duly approved by EIC for pipeline trench and banks falls under minor water body crossing as per technical specification & Std. Drg. No. MNGL/Plng./Steel/28, wherever required or, as directed by Onwer / EIC. | Item17
18 | Training and diversions of streams in steep slope area, wherever required. | Item18
19 | Carrying out air cleaning, pigging, flushing, cleaning and hydrostatic testing of complete pipeline with required quantity of corrosion inhibitor including pre-testing of designated sections complete as per specification and approved by Engineer–in–charge to specified pressures indicated elsewhere and duration after stabilization as per specification, providing all equipment, pumps, fittings, instruments, dead weight tester, pressure recorder, thermocouples etc., and services, supervision, labour, consumables, water including supply of corrosion inhibitor, air, etc. as required, locating of leaks and rectification of defect attributable to Contractor (rectification of defects in linepipe material not attributable to contractor shall be paid separately as per other item of schedule of rate), re-testing after rectification, dewatering after successful completion of hydrotesting of entire section and as per specification | Item19
20 | All tieing-in, including the tie-in(s) of the pipeline with the adjacent sections of pipeline including cutting of test header, rebevelling as required, radiography and other NDT examination, joint coating as per specification. | Item20
21 | Final clean-up of right-of-use or area disturbed by contractor during their construction activities for laying of pipeline works and disposal of debris and surplus material to designated disposal areas and backfilling of trench and compaction of the same as per satisfaction of Owner and / Or as directed by Engineer–in–charge. | Item21
22 | Installation of all burried valves (except extended stem valves) inside the valve pit and making provision to operate the valve. | Item22
23 | Preparation of as-built drawings, pipe-books (1 set of tracing on polyester film and 6 sets of as-built drawings and 1 soft copy and 6 hard copies of pipe book) All the works shall be executed in accordance with the provision of contract including carrying out all temporary/ ancillary/ auxiliary works required for the performance of the works and all other acts, deeds, matters and things necessary to make the pipeline ready for precommissioning activities. | Item23
24 | Raking up of hard surface of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. Payment for cutting of hard rock, if any, is covered unders SOR no. 96 | Item24
25 | Specified dia Thk (mm) Material Coating Type Length of each pipe (mm) NB | Item25
26 | 305 (approx.) 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item26 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
27 | 150 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item27 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
28 | 100 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item28 | 980 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
29 | Note: This item shall be applicable for the underground steel grid main pipeline & branch pipeline, barred tees, insulating joints, bends, flanges & fittings, accessories etc. (i.e. including arrangement for making provision for tap-off on proposed steel grid main pipeline) and aboveground approach pipeline upto Insulating Joint (excluding installation of aboveground insulating joint) for various stations. | Item29
30 | Items except above are covered separately. The lengths of pipelines are tentative. | Item30
31 | Permission Liasioning /Follow-up | Item31
32 | Liasioning & follow up for Permission with all the concerned authorities & boards viz Railways, NH, PWD, MIDC, Local Municipal, Panchyat, Electricity, REC, RES, Sewage water, Drinking water, Forest, Social Forestry, Owners of OFC, Traffic, Law & Order, Fire Brigade, Private Land Owner etc. for entire pipeline length and associated terminals (like SVs, tap-offs) alongwith associated work as per tender. | Item32 | 7700 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
33 | Laying of RCC Tiles | Item33
34 | Providing single layer of RCC Tiles with supply of RCC Tiles to entire width of trench above Warning Mat placed in trench over the laid pipeline as per standard drawing, specification and instruction of Owner. (Rate to include cost of all labour, tools, tackles, equipment, hire charges & supply of all materials, etc.) | Item34
35 | For width of 12" pipeline trench | Item35 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
36 | For width of 6" pipeline trench | Item36 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
37 | For width of 4" pipeline trench | Item37 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
38 | Barricading to comply with HSSE | Item38
39 | Steel barricading of the trenches Cautionary Sign Boards and lighting arrangement shall be provided as per attched drawing no.MNGL/Plng./steel/04. The rates include barricading of trenches along with sign boards, lighting etc. and maintain the same till the back filling of the trench. Rates will be payable per metre of BARRICADING PROVIDED. If proper barricading is not provided, MNGL will barricade the trenches at the risks and costs of the CONTRACTOR and will levy penalty of twice the rate per unit for the relevant section of the pipeline apart from other actions as per contract. | Item39 | 7700 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
40 | RESTORATION OF ROADS Restoration of asphalt / concrete / red stone roads / pavement/Footpath/Paver block including compaction of soil, to original condition as per requirement and to the entire satisfaction of EIC and / or concerned Owners having jurisdiction for following thickness. | Item40
41 | Restoration of Asphalt road upto 10 cm thickness | Item41 | 800 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
42 | Restoration of Asphalt road beyond 10 cm upto 20 cm thickness | Item42 | 150 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
43 | Restoration of Concrete road upto 10 cm thickness | Item43 | 600 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
44 | Restoration of red stone road / footpath / pavement/ Paverblock upto 4 cm thickness | Item44 | 600 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
45 | BORROWED SELECT SOIL FOR BACKFILLING Additional work over and above item 1.0 for supply of specified and approved quality of borrowed soft graded soil / sand in place of available excavated material and / or other suitable soil as per applicable standards / specifications, including backfilling of excavated trench for specified length after laying and padding of pipeline, including transportation of such special backfill material over all distances, complete. | Item45 | 900 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
46 | CROSSING OF STEEL PIPELINE BY OPEN CUT | Item46
47 | Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insatllation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed. | Item47
48 | Road Crossing By Open Cut Method Road Crossings at various locations by Open cut Method along with laying of MDPE upto 180 mm Dia if necessary as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item48
49 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item49 | 90 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
50 | Line pipe detail 6" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item50 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
51 | Line pipe detail 4" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item51 | 70 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
52 | Water body Crossing By Open Cut Method water/ canal/ nallah/ drain/ channel Crossings at various locations by Open cut Method along with laying of MDPE upto 180 mm Dia if necessary as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item52
53 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item53 | 90 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
54 | Line pipe detail 6" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item54 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
55 | Line pipe detail 4" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item55 | 70 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
56 | Note: Laying of the pipeline by the approved method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item56
57 | Backfilling of the Road/water/ canal/ nallah/ drain/ channel Crossings/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority. | Item57
58 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item58
59 | CROSSINGS/LAYING ALONG THE ROAD BY HDD METHOD | Item59
60 | Complete work of the any crossing (between the limits are defined as approved drawings) by HDD method including "Receiving and taking over" owner supplied three layer PE coated line pipes from Owner's designated place to issue/ dump site(s) and transportation to Contractor's stock yard/ work shop/ work site including all handling loading, unloading, aligning etc. supply of all Contractor supplied material, manpower, equipment, other resources and aquiring the required land for storage, fabrication inclduing string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type Heat Shrink Sleeve and repair of pipeline coating with special repair patch materials as per specification,pre-testing etc. of complete string made for crossing access for Contractor etc and execution of, but not limited to, following works in accordance with specifications scope of work and instructions of Engineer-in-charge and as per all provision of Contract Document. | Item60
61 | Pre-construction surveys based on site visit, collection of historical data from irrigation/ concerned department including design & calculation and detail engineering and making of crossing drawing for getting their approval from concerned Authority/ Engineer-in-charge, getting work permit/ NOC for water crossings/ road crossings as well as utility crossings (if any) encountered during crossing prior to start the execution of work. | Item61
62 | Directional drilling to required depth from top of road including maintenance of drill hole in all types of strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) at all depth to accommodate the pipeline at all conditions encountered during rail/ road crossing by approved HDD methods for providing minimum cover specified in code/ specification or the actual depth as decided by concerned authority, whichever is more. | Item62
63 | In case of water crossing, drilling to the required depth on the banks and bed including maintenance of drill hole in all types of soil strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) all depth to accommodate the pipeline a by HDD methods for providing with minimum cover over top of the pipe at all point across the maximum possible width of water bed (as per drawing) either 1.5 mtrs. below the predicted scour profile expected during the life time of the pipeline or 2.5 mtrs. below the available lowest firm bed (if scour profile/ depth not available) of the water crossing by ascertaining bed level upto 50 mtrs. both the side from crossing location or the actual depth as decided by concerned Authority/ Engineer-in-charge whichever is more. | Item63
64 | Laying of the pipeline by the approved HDD method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints with special type Dirax Heat Shrink Sleeve or equivalent and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item64
65 | Backfilling of the ditch/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority and all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specification, approved drawings, calculations, methods and to the satisfaction of Engineer-in-charge and/or as directed by concerned Authority. | Item65
66 | Post installation hydrotest dewatering and tie-in with pipeline at either side of crossing/banks etc. | Item66
67 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item67
68 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 (along with laying of 4'' Steel Pipe for MDPE if necessary) by HDD Method . | Item68 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
69 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 150 mm NB x 6.4 mm thk. of API X-52 (along with laying of 4" Steel Pipe for MDPE if necessary) by HDD Method. | Item69 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
70 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 100 mm NB x 6.4 mm thk. of API X-52 (along with laying of 4" Steel Pipe for MDPE if necessary) by HDD Method. | Item70 | 120 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
71 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item71 | 350 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
72 | Laying along the Road by carrier pipeline of size 150 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item72 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
73 | Laying along the Road by carrier pipeline of size 100 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item73 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
74 | Installation of carrier pipes by rock drilling for Road/water/Canal/ nallah/ drain/ channel/along the road, or wherever required in all types of hard rock. It includes survey of the underground utilities, submission of profile for approval, execution of the work as per the standard procedure, including , excavation of the pits, insertion/pulling of the carrier pipe, removal of malba, subsequent backfilling and restoration of the facility crossed as per original condition, including supply of all other materials, equipment, consumables, manpower etc including string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type of Heat Shrink Sleeve (Direx) and repair of pipeline coating with special repair patch materials as per Specification, pre-testing etc. of complete string made for crossing/ laying access for Contractor etc. and execution of, but not limited to, following works in accordance with specifications and instruction of Engineer-in-Charge and as per all provision of Contract Document. Balance activities as defined in SOR Item of open trench. Note:The length of HDD mentioned is tentative and may vary to the considerable extent depending upon requirements as per site conditions. The length mentioned in SOR is indicative for all the crossing to be done by HDD, numbers and locations shall be decided by Engineer-in-Charge depending upon site condition. Payment for the length of final tie-in carrier pipeline string with mainline laid by HDD are inclusive in this above item rate. No separate payment shall be made under other clauses mentioned elsewhere. Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item74
75 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 (along with laying of 4'' Steel Pipe for MDPE if necessary) by HDD Method . | Item75 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
76 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 150 mm NB x 6.4 mm thk. of API X-52 (along with laying of 4" Steel Pipe for MDPE if necessary) by HDD Method. | Item76 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
77 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 100 mm NB x 6.4 mm thk. of API X-52 (along with laying of 4" Steel Pipe for MDPE if necessary) by HDD Method. | Item77 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
78 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item78 | 150 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
79 | Laying along the Road by carrier pipeline of size 150 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item79 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
80 | Laying along the Road by carrier pipeline of size 100 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item80 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
81 | Note: (i) Crossing width & Actual string length for HDD shall vary as per design calculations & site condition so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. | Item81
82 | (ii)Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item82
83 | (iii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by HDD method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item83
84 | (iv) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossing at different locations. | Item84
85 | (v) The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. | Item85
86 | Note: (i) Quantity mentioned under item nos. 48, 52 are indicative only for different location of roads/water/ canal/ nallah/ drain/ channel Crossings. (ii) Actual length & width of individual crossing and cover from top of casing pipe/ carrier pipe string may vary depending upon site condition, approved crossing drawings, specifications etc. and / or as decided by Engineer-in-charge/ Concerned Authority. | Item86
87 | (iii) Payment for supply & installation of Zinc ribbon anode and its design excluded from above item and covered elsewhere in the SOR. (iv) Payment for the length carrier pipeline string inserted in casing pipe laid by Boring are covered separately and shall be paid under other clauses mentioned elesewhere in the SOR. | Item87
88 | Excavation beyond 1.5m depth in case of crossing of utilities/ drain/ culverts etc. through open cut upto the following depth (including restoration of the damaged area to its original condition and satisfaction of the Engineer-in-charge / concerned authorities) : - | Item88
89 | In all type of surface (Kachha/ built-up surface / Hard surface) of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. The other activities are as per SOR 1.1. Payment for cutting of hard rock, if any, is covered unders SOR no. 7.0 | Item89
90 | Deeper than 1.5 m & upto 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item90 | 700 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
91 | Deeper than 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item91 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
92 | Deeper than 1.5 m & upto 2.5 m below existing level (for 150 (approx.) mm NB Pipeline) | Item92 | 40 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
93 | Deeper than 2.5 m below existing level (for 150 (approx.) mm NB Pipeline) | Item93 | 40 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
94 | Deeper than 1.5 m & upto 2.5 m below existing level (for 100 (approx.) mm NB Pipeline) | Item94 | 300 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
95 | Deeper than 2.5 m below existing level (for 100 (approx.) mm NB Pipeline) | Item95 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
96 | Excavation of hard rock | Item96
97 | Excavation of hard rock wherever hard rock of single piece exceeding 1.0 m in length removable by pneumatic chisel/ drill as per direction of EIC. | Item97 | 3800 | Cub. M |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
98 | REPAIR OF COATING DEFECTS (NOT ATTRIBUTED TO CONTRACTOR) | Item98
99 | Repair of Holiday in Coating (Noted and recorded at the time of "receiving and taking over") Supply of all coating repair materials as per requirements of specification to be compatible with line pipe coating material, supply of all consumables, utilities, equipments and all manpower required, pipe cleaning and surface preparation, repairing of coating defects (resulting in holiday) and testing including all handling, transportation, etc. for line pipes, performing all works necessary for the completion of the works stirctly in accordance with relevant specification and instructions of Engineer-In-Charge. This rate shall be applicable per sq. cm of the exposed steel area exposed steel area. | Item99 | 2000 | Sq. cm. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
100 | PERMANENT MARKERS Supply, fabrication and installation of all types of permanent markers along the route including all associated civil works such as excavation in all types of soil, construction in all types of soil, construction of pedestals and grouting with concrete, clearing, supply and application of approved colour and quality of primer and paint, stencil letter cutting for numbers, direction, change etc., restoration of area to original condition and performing all works as per drawing, specification and instruction of engineer-in-charge. | Item100
101 | Pipeline RCC boundary / route marker as per drawing | Item101 | 120 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
102 | Pipeline warning markers with post & foundations | Item102 | 40 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
103 | Pipeline direction marker with post & foundations | Item103 | 25 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
104 | Pipeline KM with post & foundations | Item104 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
105 | HOOK -UP | Item105
106 | Hook-up of proposed pipeline by welding of final tie-in-joint with any existing laid pipeline portion of river X-ing ,existing Tap-off & battery limit of section IV including Hook-up point of the existing pipeline to be made ready for welding by cutting of flanges / valves / headers at all depth in all type of soil etc. Venting of N2 / gas / gas mixture as required purging of N2 Gas (if required), rebevelling as required, radiography and other NDT examination, joint coating as per specification.Contractor shall supply of all consumables, manpower, machinaries, materials, N2 gas etc. and carry out all works as per the provisions of Contract document and instructions of Engineer-in-charge. | Item106
107 | For 12" NB | Item107 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
108 | For 6" NB | Item108 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
109 | For 4" NB | Item109 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
110 | PRE-COMMISSIONING AND ASSISTANCE IN COMMISSIONING OF PIPELINE SYSTEM Swabbing, drying, purging with nitrogen of the complete pipeline network and the associated facilities being installed to the specified acceptance criteria, carrying out pre-commissioning works, providing assistance during the complete duration of commissioning operations for entire pipeline network system including supply of all equipment, man-power, consumables (including pigs & nitrogen required for purging with maintaining nitrogen column of mininum 10% of pipeline geometric volume) materials for all temporary works and performing all associated works, complete as per the relevant specifications, other provisions of Contract document and instructions of Engineer-in-charge. | Item110
111 | For 12" NB Pipeline | Item111 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
112 | For 6" NB Pipeline | Item112 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
113 | For 4" NB Pipeline | Item113 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
114 | IDLE TIME PRESERVATION OF PIPELINE Preservation of complete pipeline and associated facilities forming part of the pipeline as per Bid document and its maintenance including supply of all consumables, all equipment, manpower, etc. complete as per the requirements of specifications, other provisions of Contract document and instructions of Engineer-in-charge. Note : Owner reserves the right to exercise either or none of the rates below. | Item114
115 | By filling and pressurizing with nitrogen to a pressure of 2 bar(g) for a period of 3 months. | Item115
116 | For 12" NB Pipeline | Item116 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
117 | For 6" NB Pipeline | Item117 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
118 | For 4" NB Pipeline | Item118 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
119 | For every additional period of one month or part thereof | Item119
120 | For 12" NB Pipeline | Item120 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
121 | For 6" NB Pipeline | Item121 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
122 | For 4" NB Pipeline | Item122 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
123 | RCC VALVE PITS All civil works including supply of all materials, excavation of pit, piping supports including all PCC and RCC works for valves pits including pedestals with insert plates as required sealing of pipe at valve pits, providing cover etc. and finishing , clean-up and restoration of site, filling and grading of area around valve station for avoiding any local flooding of area, as per typical drawing and specification enclosed and instructions of Engineer-in-charge. In this item, instead of Brick Work, RCC will be done | Item123
124 | Valve Pit of Size 2m x 2m | Item124 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
125 | Valve Pit of Size 1.5m x 1 m | Item125 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
126 | Valve Pit of Size 1 m x 1 m | Item126 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
127 | SUPPLY OF ASSORTED PIPE, FITTINGS AND FLANGES Complete works of supply of pipes, flanges & fittings for aboveground & underground installation including all taxes, duties, transportation and inspection charges but not limited to, the following items in accordance with PMS (piping material specification), relevant specifications & drawings indicated in job specification under SCC (technical) and instructions of Engineer-in-charge and as per all provisions of the CONTRACT DOCUMENT. - Handling including lifting, transportation from Contractor Stores to CONTRACTOR's workshop for fabrication and/ or to work site for field fabrication and erection for all piping items supplied by Contractor. | Item127
128 | Carbon Steel Pipe (A 106, Seamless B-36.10/ API X 52 ) | Item128
129 | Size Rating/ Schedule | Item129
130 | 2" NB, BE Sch. 80 | Item130 | 60 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
131 | 1" NB, PE Sch. 80 | Item131 | 42 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
132 | ¾" NB, PE Sch. 160 | Item132 | 40 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
133 | Flanges | Item133
134 | Weld Neck (B-16.5, 300# A105,125 AARH, Serrated finish) | Item134
135 | Size Rating/ Schedule | Item135
136 | 6" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item136 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
137 | 4" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item137 | 5 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
138 | 2" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item138 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
139 | 3/4" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item139 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
140 | Blind Flanges (B-16.5, 300# A105,125 AARH Serrated) | Item140
141 | Size | Item141
142 | 6" NB, RF | Item142 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
143 | 4" NB, RF | Item143 | 5 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
144 | 2" NB, RF | Item144 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
145 | 3/4" NB, RF | Item145 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
146 | Elbow (Seamless) | Item146
147 | 90° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item147
148 | Size Rating/ Schedule | Item148
149 | 12" NB 300# | Item149 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
150 | 6" NB 300# | Item150 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
151 | 4" NB 300# | Item151 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
152 | 2" NB Sch. 80 | Item152 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
153 | 45° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item153
154 | Size Rating/ Schedule | Item154
155 | 12" NB 300# | Item155 | 22 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
156 | 6" NB 300# | Item156 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
157 | 4" NB 300# | Item157 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
158 | 2" NB Sch. 80 | Item158 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
159 | 90° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item159
160 | Size Rating/ Schedule | Item160
161 | 12" NB 300# | Item161 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
162 | 6" NB 300# | Item162 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
163 | 4" NB 300# | Item163 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
164 | 45° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item164
165 | Size Rating/ Schedule | Item165
166 | 12" NB 300# | Item166 | 22 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
167 | 6" NB 300# | Item167 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
168 | 4" NB 300# | Item168 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
169 | 22½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D) Min Thickness 6.4mm | Item169
170 | Size Rating/ Schedule | Item170
171 | 12" NB Sch. Std. | Item171 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
172 | 6" NB End thickness to match with pipe wall thickness | Item172 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
173 | 11½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D), Min Thickness 6.4mm | Item173
174 | Size Rating/ Schedule | Item174
175 | 12" NB 300# | Item175 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
176 | 6" NB 300# | Item176 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
177 | Tees (Seamless) | Item177
178 | Equal Tee (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item178
179 | Size Rating/ Schedule | Item179
180 | 12" NB x 12" NB x 12" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item180 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
181 | 6" NB x 6" NB x 6" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item181 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
182 | 4" NB x 4" NB x 4" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item182 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
183 | 2" NB x 2" NB x 2" NB Sch. XS | Item183 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
184 | Unequal Tee (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item184
185 | Size Rating/ Schedule | Item185
186 | 12" NB x 12" NB x 6" NB Sch. Std. x Sch. Std. | Item186 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
187 | 12" NB x 12" NB x 4" NB Sch. Std. x Sch. Std. | Item187 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
188 | 4" NB x 4" NB x 2" NB Sch. 80 x Sch.80 | Item188 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
189 | 6" NB x 6" NB x 4" NB Sch. Std.x Sch. XS | Item189 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
190 | Reducer (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item190
191 | 12" NB x 6" NB Min Thickness 6.4mm | Item191 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
192 | 12" NB x 4" NB Min Thickness 6.4mm | Item192 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
193 | 6" NB X 4" NB Min Thickness 6.4mm | Item193 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
194 | 4" NB X 2" NB Min Thickness 6.4mm | Item194 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
195 | Weldolet and Sockolet | Item195
196 | Weldolet (MOC A105 & DIM. MSS SP 97) | Item196
197 | Size Rating/ Schedule | Item197
198 | 12" NB x 2" NB Sch. 80. | Item198 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
199 | 6" NB x 2" NB Sch.80 | Item199 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
200 | 4" NB x 2" NB Sch. 80 | Item200 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
201 | Sockolet (MOC A105 & DIM. MSS SP 97) | Item201
202 | 12" NB x 3/4" NB #6000 | Item202 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
203 | 6" NB x 3/4" NB #3000 | Item203 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
204 | 6" NB x 1" NB #3000 | Item204 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
205 | 4" NB x 3/4" NB #3000 | Item205 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
206 | Butt Weld Disc End Cap (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item206
207 | Size Rating/ Schedule | Item207
208 | 12" Sch. Std. | Item208 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
209 | 6" Sch. 40 | Item209 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
210 | 4" Sch. 80 | Item210 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
211 | Fabrication & Installation of Underground Valve Assembly | Item211
212 | 12"NB Isolation Valve/tap-off assembly as per Drg. No. MNGL/Plng./Steel/40 | Item212 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
213 | 6" NB Isolation Valve/tap-off assembly as per Drg. No.MNGL/Plng./Steel/40 | Item213 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
214 | 4" NB Isolation Valve/tap-off assembly as per Drg. No. MNGL/Plng./Steel/40 | Item214 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
215 | Note: | Item215
216 | For all the supply items mentioned above, procurement shall be made as per enclosed Data Sheets and respective technical specification, after due approval of Engineer-in-charge. | Item216
217 | The quantities mentioned above are tentative and quantities for above supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item217
218 | PLANT PIPING (ABOVEGROUND) Fabrication and testing of carbon steel piping and fittings, valves, IJ, including supply of all consumables, equipment, manpower, and other resources and execution of job as per instruction AIC/EIC.Transportation of all piping items from Owner's and/ or Contractor's storage point to work at site/ workshop as applicable, complete work of fabrication, erection, painting, testing of pipes, flanges and fittings and making ready for further Commissioning / Start-up of carbon steel piping of all sizes and ratings including supply of all consumables, equipment, manpower and other resources and execution of, but not limited to, as per all provisions of the CONTRACT DOCUMENT. | Item218
219 | Fabrication including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site, cutting, edge preparation, inclusive of grinding the edges of pipes, fittings, flanges, reducers etc. to match with the matching edges of uneven thickness, wherever required, fit-up, welding of pipes and fittings like elbows, tees, reducers, weldolets, sockolets, Valves, IJ etc. flanges, vent and drain point connection, Radiography and NDT of all joints etc, including providing stubin connections, fabricated fittings and reinforcement pads etc., as required. | Item219
220 | Erection of pipes of all types and thickness at all elevations, connecting with equipment nozzle, aligning, installation and carrying out connected activities for all types of valves, all online instruments and fittings of all sizes of elbow, reducers, tees, flanges, blind flanges, spectacle blind flanges, branch connection / tapping for pressure gauges, including installation of gaskets and bolts. | Item220
221 | Erection including prior cleaning, lifting, placing on pipe sleepers and supports, overhead on racks, skids and at all elevations including installation and carrying out connected activities for all types of valves including supply and fixing of gaskets, studs/ bolts, nuts wherever required for all sizes, levelling, aligning, joining of flanges, blind flanges, connecting with equipment, nozzles, strainers, tie-in with existing piping/facilities, etc. tapping for inline instruments like pressure gauges, thermowells, sample connection, etc. | Item221
222 | Hydro testing of the piping job shall be conducted at pressure mentioned in specification for a period of 4 hours by using de-mineralised water, to check its strength. No visible leakages shall be detected during the test. Testing shall be conducted as per tender specification. | Item222
223 | Preparation of final bill of material based on piping GADs. | Item223
224 | Preparation of isometric and fabrication drawings. | Item224
225 | Carrying out Non-destructive testing as required except items mentioned in sl. no. 286 of SOR. | Item225
226 | Painting of entire system (including aboveground all pipes fittings, flanges and accessories) as per specifications suitable for highly corrosive area environment including supply of approved paints and primers, application of primer and paints, indentification lettering/ numbering, colour coding, etc. as specified including rub down & touch up of shop primer or scrapping of shop primer wherever required by COMPANY and providing scaffolding for all heights etc. | Item226
227 | Cleaning and flushing by water/ compressed air, testing of the systems including hydrostatic, pneumatic and any other type of testing as specified, draining, drying by compressed air/other methods approved by COMPANY. | Item227
228 | Precommissioning & making operational all piping system and equipments. | Item228
229 | Commissioning Contractor scope shall provide all necessary assistance in term of supply of man-power, equipment, tools and tackles required amount of nitrogen for purging of entire terminal piping system including equipments etc. to the company during commissioning activities. | Item229
230 | Completion of all such work in all respects as per scope of work and as per drawings, specifications and instructions of the COMPANY and keeping the system ready in all respects for further commissioning and start up. | Item230
231 | Hook-up works (with client/ consumer piping at battery limits): | Item231
232 | Complete Carbon Steel aboveground Piping Work with painting including all fittings, flanges and supply of all required gaskets, studs bolts & nuts etc. , and Any other work and material required for the completion of the work and not covered above and desired by EIC shall be in the scope of contractor | Item232
233 | Carbon Steel Pipe (ASTM A 106, Seamless B-36.10 / API X 52) | Item233 | 200 | inch Dia |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
234 | 1) Pipe Specification and thickness may vary depending upon availability of pipe. No extra payment shall be made for this. 2) All butt welded fittings & flanges end shall generally match with connecting pipe wall thickness. However, in case of misalignment, Contractor shall have to do end preparation without any extra cost. 3) All o-lets less than 2" NB size, all sizes of coupling and nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under erection rate. | Item234
235 | Aboveground installation of Insulating Joint & Valves etc. Handling including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site and installation of all types of valves, insulating joint including assembly of valve accessories, (if any) by bolting, threading or welding, supply and insertion of gaskets, nuts & bolts, nipples, etc. at all elevations of pipe sleepers, supports or overhead on racks, equipments nozzle, skid & painting etc. supply of all consumables, manpower, equipment, etc. for completion of all works as per scope of work and as per drawings, specifications and instructions of Engineer-in-charge including servicing/ cleaning of valve wherever requried. | Item235
236 | Welded Valves (Full Bore/ Reduced Bore) Ball / Globe / Check Valve | Item236
237 | Size Rating/ Schedule | Item237
238 | 4" NB 300# | Item238 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
239 | 2" NB 300# | Item239 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
240 | Sockolet Welded Valve (Ball / Globe Valve) | Item240
241 | Size Rating/ Schedule | Item241
242 | 1" NB 800# | Item242 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
243 | ¾" NB 800# | Item243 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
244 | 12" NB, 300# - Insulating Joints | Item244 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
245 | 6" NB, 300# - Insulating Joints | Item245 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
246 | 4" NB, 300# - Insulating Joints | Item246 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
247 | STRUCTURAL WORKS | Item247
248 | Supply of erection of single leaf mild steel gate 2.5m high with mesh upto 2m height and barbed wire fencing and 2m wide complete in all respect including painting as per TS on all MS items, all works as per specification and drawings excluding foundations and RCC beams. | Item248 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
249 | Supply of all materials, fabrication and erection of chain link fencing 2.5m high with mesh up to 2m height and barbed wire fenching complete in all respects including painting as per TS on all MS items, all works as per specification and drawings excluding foundation and RCC beams. | Item249 | 150 | RM |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
250 | Pipe Supports & Other Structures | Item250
251 | Supply, fabrication and erection of all types of pipe supports like clamps, saddle, guide stops, cradles, turn buckles, anchors, T-posts; stockade/ trestle and pipe bridge for overhead piping; frames for canopy, approach ladders and platforms, crossover, cable tray supports, etc. including painting suitable for highly corrosive area as per specification labour and supervision & complete work as per drawings, specifications and instruction of Engineerqw-incharge. (Bolts, nuts, washers, U-clamps etc. for supporting shall be supplied by the Contractor within the rates quoted. These items will not be measured and paid seperately). The work is to be completed in all respect as per scope of work and specification. | Item251 | 300 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
252 | Notes: | Item252
253 | The quantities indicated are estimated values and hence are approximate. Final payment will be made based on actual quantities to be certified by the Purchaser. | Item253
254 | The cost of MS bolts (permanent and service(, washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants etc., as required for the work shall be deemed to be included in the quoted rates. | Item254
255 | All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accrodance with time schedule, are deemed be included in the quoted rates. | Item255
256 | CIVIL WORKS | Item256
257 | Site Grading Excavation in earth and filling to the grades and levels shown in the approved drawings in all kinds of conditions including for Road embarkments, using approved quality good earth from designated borrow area, for all heights and depths including clearing and stripping (min. 150mm) of the area marked for filling, taking spot levels, consolidating the exposed natural soil surface, excavating the earth from borrow area loading, transporting & unloading, spreading in layers not exceeding 150mm thickness, breaking clods, watering (if reqd.), ramming and compacting by manual/ mechanical means to give minimum 92% of modified Proctor's density of earth, testing & dressing including disposal of all unserviceable material all complete as per specifications and directions of Engineer-in-charge. | Item257 | 150 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
258 | (Rate to include cost of all labour, tools, tackles, equipment, hire charges, cost of borrow earth by way of royalties, right of way, cess etc., as applicable with all bye works and sundry works). | Item258
259 | Plain Cement Concrete Supplying and laying plain cement concrete (including shuttering of required) in all types of concrete works including levelling courses below foundation, substructure, superstrcuture, chambers, cable tranch, under floors and any other locations, at all leveies as per drawings, specifications and directions of the Engineer-in-charge. | Item259
260 | PCC 1:2:4 1 Cement : 2 Coarse sand : 4 stone aggregate 20mm nominal size. | Item260 | 400 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
261 | Reinforced Cement Concrete Providing and laying reinforced cement of grade M-20 with 20mm and down grade crushed stone aggregate in all types of structures like foundations, pedestals, pedestal bases, pipe supports, sleepers cable trench inlcuding constrcution joints, bitumen painting on surface in contact with soil, providing and fixing reinforcing steel, shuttering, inserts, finishes etc. at all depths and heights complete as per drawings, specifications and direction of the Engineer-incharge. | Item261 | 300 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
262 | Rate to include cost of all labour, tools, tackles, equipment, hire charges, supply of all maerials such as minimum 43 grade cement including sulphate resistant cement for substructures, R/F steel, Inserts, bolts, conduits, bitumen, other minor constrcution materials, shuttering, stanging, earthwork in excavation and backfilling using serviceable earth in all conditions, shorting bailing and pumping out water, testing of concrete, curing etc. with all bye works and syndry works. | Item262
263 | TEMPORARY CATHODIC PROTECTION SYSTEM | Item263
264 | Design, detailed engineering, supply, installation, testing and commissioning of the temporary Cathodic protection system using Mg/ Zn galvanic anodes to protect the external surface of 3 LPE coated entire 5.5 km (approx.) long steel pipeline network against corrosion for design life of minimum 1 year or till commissioning of PCP system whichever is later as per standard specification No. MNGL/Steel/TS/15 for temporary cathodic protection system. Scope shall also include but not limited to the following for completion of jobs: | Item264
265 | Measurement of soil resistivity along the right of way of the main pipeline route as per specification for design & installation of anodes. | Item265
266 | Collection of additional data related to cathodic protection along the right of way of pipeline as per specifications. | Item266
267 | Supply, installation, testing & commissioning of one set of spark gap arrestor with 2 plate Zinc grounding cell of 20 kg net weight each across each insulating joint as per specification. | Item267
268 | Supply, installation, testing & commissioning one set of polarisation cell with zinc anode at all high tension (66KV or higher) electrical power transmission line/Equipment crossing or running parallel to the pipeline for grounding purpose as per specification. The rating shall depend upon anticipated fault current & ground bed resistance at the location of installation. However, the rating of polarisation cell (krick) shall not be less than 5 KA & number of 20 kg net weight zinc anode shall not be less than two. | Item268
269 | Supply & installation of Zinc Ribbon Anodes at 4-8 O’Clock position in the interval of 2 metre (max.) on carrier pipes at all cased crossings i.e. railways/ roads etc. | Item269
270 | Monitoring of the protection system for 6 months. | Item270
271 | All civil/ structural works related to TCP system including supply of bricks, cement & steel etc. required for completion of the system. | Item271
272 | For 12" | Item272 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
273 | For 6" | Item273 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
274 | For 4" | Item274 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
275 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item275
276 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item276
277 | FIELD INSTRUMENTATION | Item277
278 | PRESSURE INSTRUMENTS | Item278
279 | Supply , Installation of Pressure Gagues and their accessories inclusive of supply of necessary piping materials and tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/ manifolds & hydraulic testing (exclusive of calibration of instruments) as per installation standard attached elsewhere in Tender Document and Supply as per Data Sheet No.MEC/23K8/05/E5/I/001/DS-PG. Give breakup of supply and Installation rate. | Item279 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
280 | CALIBRATION | Item280
281 | Calibration of the instruments listed below including removal of instruments from pre-installed locations like panels, enclosure racks, fields etc. and refixing them back in respective/ required places, providing equipments, necessary test jigs, instrument air and all consumables. Calibration reports shall be prepared and to be submitted to the Purchaser/ Consultant. | Item281
282 | Pressure Gauges | Item282 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
283 | Note: | Item283
284 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item284
285 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item285
286 | Laying of MDPE pipe along with Steel pipe line Excluding supply of all MDPE pipe (PE 80/100,SDR11), but Including supply of Bends, Couplers, End caps, Tees, PE Reducer, CS to PE Fitting, Saddle Tapping, Warming mat, etc. as required to complete the job. ( Particular job specification.) "Receiving and taking-over" as defined in the specification, handling, loading, transportation and unloading of Owner supplied MDPE line pipes (PE80/100, SDR11) of all sizes (as free issue items) from Owner's designated place(s) of issue to Contractor's own stock-yard(s)/ Work Shop(s)/ work-site(s) including proper storing, stacking, identification, providing security & insurance cover , including supply of accessories of all sizes & thickness like Bends, Couplers, End caps, Tee, PE Reducer, CS to PE Fittings, Saddle Tapping, Warning Mat, etc.. | Item286
287 | Stringing/ uncoiling of the MDPE line pipe on the pipeline Right-of-Use, laying/ installation of MDPE line pipe alongwith steel pipeline (alongwith installation of required accessories as mentioned above) of following sizes, including executing all works; fabrication, access for construction; supply of all materials (except Owner supplied materials), consumables, labour and other incidental works and handing over the same after return of the surplus pipes to the Owner's designated stockyard(s); carrying out all temporary, ancillary, auxiliary works required to make the MDPE pipeline ready for commissioning as per drawings, specifications, scope of work indicated in PJS and other provisions of Contract document and instructions of Engineer-in-charge. | Item287
288 | UP to Dia 90mm | Item288 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
289 | Dia 125mm | Item289 | 5000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
290 | Note : The quantities indicated above against all individual item are tentative and may vary considerably depending upon site condition, methodology adopted as per site requirement with due approval of Owner/ Consultants. | Item290
291 | PIPING WORKS FOR SECTIONALISING VALVE STATION-CUM-TAP-OFF POINT All works for fabriaction and installation of all piping above ground at all elevations and below ground at all depth for Sectionalising Valve Station alongwith preparation of construction drawings duly approved by EIC, in all type of terrains and soils including transportation and handling of all Owner supplied materials i.e. extended stem butt welded sectionalising gas actuated ball valve, other types of valves, line pipes for mainline, 4" NB pipe for all branch line including ventlines from Owner's designated place(s) of issue to work site. | Item291
292 | Contractor shall supply all required size & type of piping material like pipes, fittings & flanges etc. as per PMS alongwith 2" NB pipe for all branch line & vent line (wherever required) including supply of all consumables, manpower, machinaries, materials etc. and carrying out all mechanical works of underground and above ground piping including fabrication, welding, nondestructive testing of welds, weld repairs/ retesting, cleaning/ flushing, pre-hydrotesting & hydrostatic testing, dewatering, functional testing, cutting of mainline and bevelling (if required) | Item292
293 | assembly, including radiography of tie-in joints, corrosion, coating and external painting as required, installation of instruments like pressure/ temperature instruments/ gauges alongwith complete SS Tubing works including supply of SS Tube and thier accessories etc., as required, obtaining all statutory clearances, approvals and permissions for the works (wherever required), making of valve pit (for detail refer relevant drawings) for SV Stationscum- tap-off points enclosed with tender filled with sand, excavation and filling in all types of soils including soft/ hard rock for installation of piping/ pipe supports providing pipe supports, area fencing and gate including all associated civil and structural works; painting, finishing, clean-up and restoration of site; preparation of as-built drawings, documents and project records and performing all works as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge. In this item, instead of Brick Work RCC will be done | Item293
294 | Type - I SV Station on 12" Pipeline | Item294 | 1 | Lumpsum for each |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
295 | Note: i) Work under above items are exclusive of all works associated with main pipeline covered under Item No. 1.0 above. ii) All civil/ structural works including area fencing and gate, valve pits except for piping support will be paid separately as per unit rate provided elsewhere in the SOR. iii) All coupling, nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under above item rate. | Item295
296 | Details of Major Road Crossing (Canal/SH/DR/NHAI): Supply, Installation & Insertion of pipeline across Canal / State Highways as per SCC and technical specifications | Item296
297 | Supply & Installation of 24" NB x 6.4mm Wall thk. Casing pipe for Line Pipe 12"NB(6.4 mm thk API 5L Gr X52) & 4" NB, 6.4 mm thk API 5L Gr. X52 pipe by Jacking Boring . Including Insertion of 12" dia and 4" dia (for 125 mm dia MDPE Connectivity) Carrier pipeline in 24" dia casing pipe and connectivity with existing pipeline at both end of National Highways/State Highways/ Railway as per SCC and technical specifications -Supply of Casing Pipe Supply of following casing pipe including handling, loading, transportation & unloading etc. to contractor's own stock yard / worksite(s). -After Completion of insertion of carrier pipe with Connectivity at both end including all works as per the scope of work -Post Hydro testing & Commissioning , Submission of as-built drawing, Submission of Documents - The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. - Rate Should include supply & installation of 250mm Casing pipe for 4" Steel Pipeline for MDPE (if required by Authority & as per the instructions of EIC) | Item297
298 | Note: (i) Crossing width may vary as per site condition. Tenderer are advised to visit site for actual assessment of extent of crossing. Actual length of Boring shall be as per design calculations so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. (ii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by Boring method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item298
299 | (iii) The Contractor has to quote alongwith 4" NB (for 125mm MDPE). No any extra payment shall be made against this item. (iv) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossings at different locations. | Item299
300 | (v) Actual length & cover from top of casing pipe string may vary depending upon site conditions, approved drawings, specification etc. and / or as decided by concerned Authority / Engineer-in-charge. (vi) No Extra Payment for supply & installation of Zinc ribbon to be provided to Carrier pipe & Zinc Anode is to be provided to Casing pipe and its design included in above item | Item300
301 | Supply and installation of 24'' casing pipe,Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insertion of carrier pipe in casing pipe after above ground pretesting at specified test pressure and installation of casing insulators & Zinc ribbon anode as per specification/ drawings. Installation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed (Any type of soil) | Item301 | 80 | Mtrs |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
Total in Figures | [51 empty] | 0 | 0 | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## BoQ7 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR | [49 empty] | 1
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Maharastra Natural Gas Ltd.,Pune
Name of Work: TENDER FORLAYING & CONSTRUCTION OF 12” NB X 6 KM U/G STEEL PIPELINE NETWORK & ASSOCIATED WORKS FROM NEAR RAIGAON BRIDGE, RAIGAON TO NEAR BAN VILLAGE ROAD, BAN (Section No-07)
Tender No: MNGL/CP/2024-25/109
Do you want to quote for this sheet ? |  |  | Yes
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE / SCHEDULE OF RATES (SOR) (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Rate inclusive of all taxes and duties except Goods & Service Tax (Rs.) | Per Unit Goods & Service Tax (GST) In % (To be entered by the Bidder) | GST in Rs. | Unit rate inclusive of all taxes & duties including GST (Rs.) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | CARBON STEEL PIPES | Item1
2 | PIPELINE LAYING / INSTALLATION in all type of surface (Normal/built-up surface) "Receiving and taking over" as defined in the specifications, handing, loading, transportation and unloading of Owner supplied 3-Layer PE coated linepipes from Owner's designated stack-yard to Contractor's stock yard/workshop/work-site including preliminary activities, preparation of drawings, wherever required for crossing etc. including handling, stacking, stringing on the pipeline Right-of-Use/ pipeline route alignment, carrying out inspection of company supplied materials including linepipes at the time of taking over, laying/ installation of coated linepipes, associated burried valves, barred tees, insulating joints, flanges & fittings of all sizes, thickness & ANSI class rating and accessories as per specification wherever required depending on site condition including execution of all works, "taking over", handling , including loading and unloading, transportation of Owner supplied materials other than linepipe from Owner's designated place (s) of issue to work site, | Item2 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3 | additional lands required for Contractor's storage, fabrication, access for construction, procurement and supply of all materials (except Owner supplied materials), consumables, equipment, labour and other inputs, carrying out all temporary, ancillary, auxiliary works, aquistion of ROU/ROW for laying of pipeline from HDD Exit and entry point to Tie in Point of existing Pipeline/ ROU, ready for commissioning of pipeline as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge, including but not limited to carrying out the following works: | Item3 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4 | Surveying of route and detours required at the time of execution including marking the same in topographical sheet, preparation of construction drawings showing survey details, and submit same to Owner for review / approval. | Item4
5 | Staking and installation of construction markers, clearing, fencing, grubbing, cutting of trees, full filling all the requirements of various statutory/ environment authorities to the entire satisfaction of concerned authorities, grading of work area. Shifting of all obstruction within the ROU/ Pipeline route alignment viz. electrical lines/ poles, telephone line / poles, etc. coordination with concerned authorities and obtain permissions from these authorities. | Item5
6 | Trenching to all depths by excavation in all types of soils including soft/ hard rock and different type of pavement / footpath / roads etc. including rock breaking, chiselling or otherwise cutting etc. as required and storing excavated soil, reusable materials at designated area as directed by Engineer in charge and to a width to accommodate the Steel pipeline as per the relevant standard/ specification etc. [The minimum depth of the top of pipeline shall be 1.0m measured from top of pipeline coating to the top of undisturbed surface of the soil or as per SCC/ OISD - 141 / 226, whichever is higher]. Dewater of trenches if required as per site condition. | Item6
7 | Carrying out repairs of pipe defects/ replacement in case of irreparable defects and repairs of defects of pipe coating not attributable to Owner including defects/ damages occurring during transportation / handling. | Item7
8 | Stringing of line pipes along pipeline trench / ROU on straw / sand / soft soil bags including supply of bags and its filling materials. | Item8
9 | Checking, cleaning, aligning, bending, cutting and bevelling (as required) of pipes for welding and field adjustments including pipe fittings, welding, carrying out non-destructive testing of welds as required including 100% radiography by X-ray and providing all requisite equipment, labour, supervision, materials, films, consumables, all facilities and personnel to process, develop, examine and interpret radiographs and other tests as required, carrying out repairs of weld joints found defective by Engineer-in-Charge, carrying out re-radiography and other tests as required on repaired joints. | Item9
10 | Carrying out installation of carrier line pipe at all minor crossing viz. carttrack, pathway, water bodies etc. at designated depth by open cut (except at crossing by HDD method). | Item10
11 | Carrying out installation of carrier line pipe in the casing pipe at cased crossing (excluding installation of casing pipes which is covered separately). | Item11
12 | Coating of field weld joints, long radius bends (R=3D), elbows, buried fittings and valves etc. including supply of coating materials etc. (i.e. heat shrinkable sleeves and high build epoxy etc.) as per PJS & Technical Specification compatible with 3 layer PE coating material of the line pipe. | Item12 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
13 | Counting the number and type of trees cut in presence of DFO/concerned authorities and keeping record thereof, stacking and handing over of all cut tress. | Item13
14 | Installation / lowering the pipeline in trench to required depth as per PJS, Techanical Specification & drawings, supply & placement of 1.0mm thk. HDPE Yellow colour warning mat,RCC tiles (300 mm width x 50 mm thick) over the pipeline Pipe in same trench along the complete route as per standard drawings, data sheets & technical specifications, padding around pipeline as per Standard Drg. no. MNGL/Plng./Steel/03 with suitable soil duly approved by EIC including supply of padding material, backfilling and its compaction to the satisfaction of concerned authorities with excavated earth / borrowed select soil including supply of borrowed select soil duly approved by EIC before backfilling and make ready for restoration to be done by Onwer / concerned authorities. | Item14
15 | Supply and installation of slope breakers, wherever required or, as directed by Onwer / Engineer–in–charge. | Item15
16 | Crossing the all-foreign pipeline / HT line / cable / any other utilities etc. with necessary concrete / HDPE sheet protection including coordination with all agencies and obtaining NOC | Item16
17 | Supply and installation of bank protection alongwith backfill materials duly approved by EIC for pipeline trench and banks falls under minor water body crossing as per technical specification & Std. Drg. No. MNGL/Plng./Steel/28, wherever required or, as directed by Onwer / EIC. | Item17
18 | Training and diversions of streams in steep slope area, wherever required. | Item18
19 | Carrying out air cleaning, pigging, flushing, cleaning and hydrostatic testing of complete pipeline with required quantity of corrosion inhibitor including pre-testing of designated sections complete as per specification and approved by Engineer–in–charge to specified pressures indicated elsewhere and duration after stabilization as per specification, providing all equipment, pumps, fittings, instruments, dead weight tester, pressure recorder, thermocouples etc., and services, supervision, labour, consumables, water including supply of corrosion inhibitor, air, etc. as required, locating of leaks and rectification of defect attributable to Contractor (rectification of defects in linepipe material not attributable to contractor shall be paid separately as per other item of schedule of rate), re-testing after rectification, dewatering after successful completion of hydrotesting of entire section and as per specification | Item19
20 | All tieing-in, including the tie-in(s) of the pipeline with the adjacent sections of pipeline including cutting of test header, rebevelling as required, radiography and other NDT examination, joint coating as per specification. | Item20
21 | Final clean-up of right-of-use or area disturbed by contractor during their construction activities for laying of pipeline works and disposal of debris and surplus material to designated disposal areas and backfilling of trench and compaction of the same as per satisfaction of Owner and / Or as directed by Engineer–in–charge. | Item21
22 | Installation of all burried valves (except extended stem valves) inside the valve pit and making provision to operate the valve. | Item22 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
23 | Preparation of as-built drawings, pipe-books (1 set of tracing on polyester film and 6 sets of as-built drawings and 1 soft copy and 6 hard copies of pipe book) All the works shall be executed in accordance with the provision of contract including carrying out all temporary/ ancillary/ auxiliary works required for the performance of the works and all other acts, deeds, matters and things necessary to make the pipeline ready for precommissioning activities. | Item23 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
24 | Raking up of hard surface of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. Payment for cutting of hard rock, if any, is covered unders SOR no. 76 | Item24 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
25 | Specified dia Thk (mm) Material Coating Type Length of each pipe (mm) NB | Item25 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
26 | 305 (approx.) 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item26 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
27 | Note: This item shall be applicable for the underground steel grid main pipeline & branch pipeline, barred tees, insulating joints, bends, flanges & fittings, accessories etc. (i.e. including arrangement for making provision for tap-off on proposed steel grid main pipeline) and aboveground approach pipeline upto Insulating Joint (excluding installation of aboveground insulating joint) for various stations. | Item27
28 | Items except above are covered separately. The lengths of pipelines are tentative. | Item28 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
29 | Permission Liasioning /Follow-up | Item29 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
30 | Liasioning & follow up for Permission with all the concerned authorities & boards viz Railways, NH, PWD, MIDC, Local Municipal, Panchyat, Electricity, REC, RES, Sewage water, Drinking water, Forest, Social Forestry, Owners of OFC, Traffic, Law & Order, Fire Brigade, Private Land Owner etc. for entire pipeline length and associated terminals (like SVs, tap-offs) alongwith associated work as per tender. | Item30 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
31 | Laying of RCC Tiles | Item31 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
32 | Providing single layer of RCC Tiles with supply of RCC Tiles to entire width of trench above Warning Mat placed in trench over the laid pipeline as per standard drawing, specification and instruction of Owner. (Rate to include cost of all labour, tools, tackles, equipment, hire charges & supply of all materials, etc.) | Item32
33 | For width of 12" pipeline trench | Item33 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
34 | Barricading to comply with HSSE | Item34 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
35 | Steel barricading of the trenches Cautionary Sign Boards and lighting arrangement shall be provided as per attched drawing no.MNGL/Plng./steel/04. The rates include barricading of trenches along with sign boards, lighting etc. and maintain the same till the back filling of the trench. Rates will be payable per metre of BARRICADING PROVIDED. If proper barricading is not provided, MNGL will barricade the trenches at the risks and costs of the CONTRACTOR and will levy penalty of twice the rate per unit for the relevant section of the pipeline apart from other actions as per contract. | Item35 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
36 | RESTORATION OF ROADS Restoration of asphalt / concrete / red stone roads / pavement/Footpath/Paver block including compaction of soil, to original condition as per requirement and to the entire satisfaction of EIC and / or concerned Owners having jurisdiction for following thickness. | Item36 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
37 | Restoration of Asphalt road upto 10 cm thickness | Item37 | 800 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
38 | Restoration of Asphalt road beyond 10 cm upto 20 cm thickness | Item38 | 200 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
39 | Restoration of Concrete road upto 10 cm thickness | Item39 | 800 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
40 | Restoration of red stone road / footpath / pavement/ Paverblock upto 4 cm thickness | Item40 | 700 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
41 | BORROWED SELECT SOIL FOR BACKFILLING Additional work over and above item 1.0 for supply of specified and approved quality of borrowed soft graded soil / sand in place of available excavated material and / or other suitable soil as per applicable standards / specifications, including backfilling of excavated trench for specified length after laying and padding of pipeline, including transportation of such special backfill material over all distances, complete. | Item41 | 900 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
42 | CROSSING OF STEEL PIPELINE BY OPEN CUT | Item42
43 | Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insatllation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed. | Item43
44 | Road Crossing By Open Cut Method Road Crossings at various locations by Open cut Method as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item44 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
45 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method | Item45 | 90 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
46 | Water body Crossing By Open Cut Method water/ canal/ nallah/ drain/ channel Crossings at various locations by Open cut Method as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item46 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
47 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method | Item47 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
48 | Note: Laying of the pipeline by the approved method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item48
49 | Backfilling of the Road/water/ canal/ nallah/ drain/ channel Crossings/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority. | Item49
50 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item50 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
51 | CROSSINGS/LAYING ALONG THE ROAD BY HDD METHOD | Item51
52 | Complete work of the any crossing (between the limits are defined as approved drawings) by HDD method including "Receiving and taking over" owner supplied three layer PE coated line pipes from Owner's designated place to issue/ dump site(s) and transportation to Contractor's stock yard/ work shop/ work site including all handling loading, unloading, aligning etc. supply of all Contractor supplied material, manpower, equipment, other resources and aquiring the required land for storage, fabrication inclduing string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type Heat Shrink Sleeve and repair of pipeline coating with special repair patch materials as per specification,pre-testing etc. of complete string made for crossing access for Contractor etc and execution of, but not limited to, following works in accordance with specifications scope of work and instructions of Engineer-in-charge and as per all provision of Contract Document. | Item52
53 | Pre-construction surveys based on site visit, collection of historical data from irrigation/ concerned department including design & calculation and detail engineering and making of crossing drawing for getting their approval from concerned Authority/ Engineer-in-charge, getting work permit/ NOC for water crossings/ road crossings as well as utility crossings (if any) encountered during crossing prior to start the execution of work. | Item53 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
54 | Directional drilling to required depth from top of road including maintenance of drill hole in all types of strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) at all depth to accommodate the pipeline at all conditions encountered during rail/ road crossing by approved HDD methods for providing minimum cover specified in code/ specification or the actual depth as decided by concerned authority, whichever is more. | Item54 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
55 | In case of water crossing, drilling to the required depth on the banks and bed including maintenance of drill hole in all types of soil strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) all depth to accommodate the pipeline a by HDD methods for providing with minimum cover over top of the pipe at all point across the maximum possible width of water bed (as per drawing) either 1.5 mtrs. below the predicted scour profile expected during the life time of the pipeline or 2.5 mtrs. below the available lowest firm bed (if scour profile/ depth not available) of the water crossing by ascertaining bed level upto 50 mtrs. both the side from crossing location or the actual depth as decided by concerned Authority/ Engineer-in-charge whichever is more. | Item55 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
56 | Laying of the pipeline by the approved HDD method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints with special type Dirax Heat Shrink Sleeve or equivalent and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item56 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
57 | Backfilling of the ditch/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority and all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specification, approved drawings, calculations, methods and to the satisfaction of Engineer-in-charge and/or as directed by concerned Authority. | Item57 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
58 | Post installation hydrotest dewatering and tie-in with pipeline at either side of crossing/banks etc. | Item58 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
59 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item59 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
60 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 by HDD Method . | Item60 | 120 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
61 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item61 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
62 | Installation of carrier pipes by rock drilling for Road/water/Canal/ nallah/ drain/ channel/along the road, or wherever required in all types of hard rock. It includes survey of the underground utilities, submission of profile for approval, execution of the work as per the standard procedure, including , excavation of the pits, insertion/pulling of the carrier pipe, removal of malba, subsequent backfilling and restoration of the facility crossed as per original condition, including supply of all other materials, equipment, consumables, manpower etc including string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type of Heat Shrink Sleeve (Direx) and repair of pipeline coating with special repair patch materials as per Specification, pre-testing etc. of complete string made for crossing/ laying access for Contractor etc. and execution of, but not limited to, following works in accordance with specifications and instruction of Engineer-in-Charge and as per all provision of Contract Document. Balance activities as defined in SOR Item of open trench. Note:The length of HDD mentioned is tentative and may vary to the considerable extent depending upon requirements as per site conditions. The length mentioned in SOR is indicative for all the crossing to be done by HDD, numbers and locations shall be decided by Engineer-in-Charge depending upon site condition. Payment for the length of final tie-in carrier pipeline string with mainline laid by HDD are inclusive in this above item rate. No separate payment shall be made under other clauses mentioned elsewhere. Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item62
63 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 by HDD Method . | Item63 | 130 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
64 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item64 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
65 | Note: (i) Crossing width & Actual string length for HDD shall vary as per design calculations & site condition so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. | Item65
66 | (ii)Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item66
67 | (iii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by HDD method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item67
68 | (iv) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossing at different locations. | Item68
69 | (v) The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. | Item69
70 | Note: (i) Quantity mentioned under item nos. 44, 46 are indicative only for different location of roads/water/ canal/ nallah/ drain/ channel Crossings. (ii) Actual length & width of individual crossing and cover from top of casing pipe/ carrier pipe string may vary depending upon site condition, approved crossing drawings, specifications etc. and / or as decided by Engineer-in-charge/ Concerned Authority. | Item70
71 | (iii) Payment for supply & installation of Zinc ribbon anode and its design excluded from above item and covered elsewhere in the SOR. (iv) Payment for the length carrier pipeline string inserted in casing pipe laid by Boring are covered separately and shall be paid under other clauses mentioned elesewhere in the SOR. | Item71
72 | Excavation beyond 1.5m depth in case of crossing of utilities/ drain/ culverts etc. through open cut upto the following depth (including restoration of the damaged area to its original condition and satisfaction of the Engineer-in-charge / concerned authorities) : - | Item72 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
73 | In all type of surface (Kachha/ built-up surface / Hard surface) of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. The other activities are as per SOR 1.1. Payment for cutting of hard rock, if any, is covered unders SOR no. 76 | Item73
74 | Deeper than 1.5 m & upto 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item74 | 800 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
75 | Deeper than 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item75 | 500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
76 | Excavation of hard rock | Item76
77 | Excavation of hard rock wherever hard rock of single piece exceeding 1.0 m in length removable by pneumatic chisel/ drill as per direction of EIC. | Item77 | 3800 | Cub. M |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
78 | REPAIR OF COATING DEFECTS (NOT ATTRIBUTED TO CONTRACTOR) | Item78
79 | Repair of Holiday in Coating (Noted and recorded at the time of "receiving and taking over") Supply of all coating repair materials as per requirements of specification to be compatible with line pipe coating material, supply of all consumables, utilities, equipments and all manpower required, pipe cleaning and surface preparation, repairing of coating defects (resulting in holiday) and testing including all handling, transportation, etc. for line pipes, performing all works necessary for the completion of the works stirctly in accordance with relevant specification and instructions of Engineer-In-Charge. This rate shall be applicable per sq. cm of the exposed steel area exposed steel area. | Item79 | 2200 | Sq. cm. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
80 | PERMANENT MARKERS Supply, fabrication and installation of all types of permanent markers along the route including all associated civil works such as excavation in all types of soil, construction in all types of soil, construction of pedestals and grouting with concrete, clearing, supply and application of approved colour and quality of primer and paint, stencil letter cutting for numbers, direction, change etc., restoration of area to original condition and performing all works as per drawing, specification and instruction of engineer-in-charge. | Item80
81 | Pipeline RCC boundary / route marker as per drawing | Item81 | 120 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
82 | Pipeline warning markers with post & foundations | Item82 | 40 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
83 | Pipeline direction marker with post & foundations | Item83 | 25 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
84 | Pipeline KM with post & foundations | Item84 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
85 | HOOK -UP | Item85
86 | Hook-up of proposed pipeline by welding of final tie-in-joint with any existing laid pipeline portion of river X-ing ,existing Tap-off & battery limit of section IV including Hook-up point of the existing pipeline to be made ready for welding by cutting of flanges / valves / headers at all depth in all type of soil etc. Venting of N2 / gas / gas mixture as required purging of N2 Gas (if required), rebevelling as required, radiography and other NDT examination, joint coating as per specification.Contractor shall supply of all consumables, manpower, machinaries, materials, N2 gas etc. and carry out all works as per the provisions of Contract document and instructions of Engineer-in-charge. | Item86
87 | For 12" NB | Item87 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
88 | PRE-COMMISSIONING AND ASSISTANCE IN COMMISSIONING OF PIPELINE SYSTEM Swabbing, drying, purging with nitrogen of the complete pipeline network and the associated facilities being installed to the specified acceptance criteria, carrying out pre-commissioning works, providing assistance during the complete duration of commissioning operations for entire pipeline network system including supply of all equipment, man-power, consumables (including pigs & nitrogen required for purging with maintaining nitrogen column of mininum 10% of pipeline geometric volume) materials for all temporary works and performing all associated works, complete as per the relevant specifications, other provisions of Contract document and instructions of Engineer-in-charge. | Item88
89 | For 12" NB Pipeline | Item89 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
90 | IDLE TIME PRESERVATION OF PIPELINE Preservation of complete pipeline and associated facilities forming part of the pipeline as per Bid document and its maintenance including supply of all consumables, all equipment, manpower, etc. complete as per the requirements of specifications, other provisions of Contract document and instructions of Engineer-in-charge. Note : Owner reserves the right to exercise either or none of the rates below. | Item90
91 | By filling and pressurizing with nitrogen to a pressure of 2 bar(g) for a period of 3 months. | Item91 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
92 | For 12" NB Pipeline | Item92 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
93 | For every additional period of one month or part thereof | Item93 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
94 | For 12" NB Pipeline | Item94 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
95 | RCC VALVE PITS All civil works including supply of all materials, excavation of pit, piping supports including all PCC and RCC works for valves pits including pedestals with insert plates as required sealing of pipe at valve pits, providing cover etc. and finishing , clean-up and restoration of site, filling and grading of area around valve station for avoiding any local flooding of area, as per typical drawing and specification enclosed and instructions of Engineer-in-charge. In this item, instead of Brick Work, RCC will be done | Item95 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
96 | Valve Pit of Size 2m x 2m | Item96 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
97 | SUPPLY OF ASSORTED PIPE, FITTINGS AND FLANGES Complete works of supply of pipes, flanges & fittings for aboveground & underground installation including all taxes, duties, transportation and inspection charges but not limited to, the following items in accordance with PMS (piping material specification), relevant specifications & drawings indicated in job specification under SCC (technical) and instructions of Engineer-in-charge and as per all provisions of the CONTRACT DOCUMENT. - Handling including lifting, transportation from Contractor Stores to CONTRACTOR's workshop for fabrication and/ or to work site for field fabrication and erection for all piping items supplied by Contractor. | Item97
98 | Carbon Steel Pipe (A 106, Seamless B-36.10/ API X 52 ) | Item98
99 | Size Rating/ Schedule | Item99 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
100 | 2" NB, BE Sch. 80 | Item100 | 55 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
101 | 1" NB, PE Sch. 80 | Item101 | 36 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
102 | ¾" NB, PE Sch. 160 | Item102 | 32 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
103 | Flanges | Item103
104 | Weld Neck (B-16.5, 300# A105,125 AARH, Serrated finish) | Item104
105 | Size Rating/ Schedule | Item105 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
106 | 2" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item106 | 10 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
107 | Blind Flanges (B-16.5, 300# A105,125 AARH Serrated) | Item107
108 | Size | Item108
109 | 2" NB, RF | Item109 | 10 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
110 | Elbow (Seamless) | Item110 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
111 | 90° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item111
112 | Size Rating/ Schedule | Item112
113 | 12" NB 300# | Item113 | 25 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
114 | 45° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item114 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
115 | Size Rating/ Schedule | Item115
116 | 12" NB 300# | Item116 | 22 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
117 | 90° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item117 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
118 | Size Rating/ Schedule | Item118
119 | 12" NB 300# | Item119 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
120 | 45° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item120
121 | Size Rating/ Schedule | Item121
122 | 12" NB 300# | Item122 | 22 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
123 | 22½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D) Min Thickness 6.4mm | Item123 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
124 | Size Rating/ Schedule | Item124
125 | 12" NB Sch. Std. | Item125 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
126 | 11½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D), Min Thickness 6.4mm | Item126
127 | Size Rating/ Schedule | Item127
128 | 12" NB 300# | Item128 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
129 | Tees (Seamless) | Item129
130 | Equal Tee (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item130
131 | Size Rating/ Schedule | Item131
132 | 12" NB x 12" NB x 12" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item132 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
133 | 2" NB x 2" NB x 2" NB Sch. XS | Item133 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
134 | Weldolet and Sockolet | Item134
135 | Weldolet (MOC A105 & DIM. MSS SP 97) | Item135
136 | Size Rating/ Schedule | Item136
137 | 12" NB x 2" NB Sch. 80. | Item137 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
138 | Sockolet (MOC A105 & DIM. MSS SP 97) | Item138
139 | 12" NB x 3/4" NB #6000 | Item139 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
140 | Butt Weld Disc End Cap (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item140
141 | Size Rating/ Schedule | Item141
142 | 12" Sch. Std. | Item142 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
143 | Fabrication & Installation of Underground Valve Assembly | Item143 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
144 | 12"NB Isolation Valve/tap-off assembly as per Drg. No. MNGL/Plng./Steel/40 | Item144 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
145 | Note: | Item145 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
146 | For all the supply items mentioned above, procurement shall be made as per enclosed Data Sheets and respective technical specification, after due approval of Engineer-in-charge. | Item146
147 | The quantities mentioned above are tentative and quantities for above supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item147
148 | PLANT PIPING (ABOVEGROUND) Fabrication and testing of carbon steel piping and fittings, valves, IJ, including supply of all consumables, equipment, manpower, and other resources and execution of job as per instruction AIC/EIC.Transportation of all piping items from Owner's and/ or Contractor's storage point to work at site/ workshop as applicable, complete work of fabrication, erection, painting, testing of pipes, flanges and fittings and making ready for further Commissioning / Start-up of carbon steel piping of all sizes and ratings including supply of all consumables, equipment, manpower and other resources and execution of, but not limited to, as per all provisions of the CONTRACT DOCUMENT. | Item148 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
149 | Fabrication including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site, cutting, edge preparation, inclusive of grinding the edges of pipes, fittings, flanges, reducers etc. to match with the matching edges of uneven thickness, wherever required, fit-up, welding of pipes and fittings like elbows, tees, reducers, weldolets, sockolets, Valves, IJ etc. flanges, vent and drain point connection, Radiography and NDT of all joints etc, including providing stubin connections, fabricated fittings and reinforcement pads etc., as required. | Item149 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
150 | Erection of pipes of all types and thickness at all elevations, connecting with equipment nozzle, aligning, installation and carrying out connected activities for all types of valves, all online instruments and fittings of all sizes of elbow, reducers, tees, flanges, blind flanges, spectacle blind flanges, branch connection / tapping for pressure gauges, including installation of gaskets and bolts. | Item150 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
151 | Erection including prior cleaning, lifting, placing on pipe sleepers and supports, overhead on racks, skids and at all elevations including installation and carrying out connected activities for all types of valves including supply and fixing of gaskets, studs/ bolts, nuts wherever required for all sizes, levelling, aligning, joining of flanges, blind flanges, connecting with equipment, nozzles, strainers, tie-in with existing piping/facilities, etc. tapping for inline instruments like pressure gauges, thermowells, sample connection, etc. | Item151
152 | Hydro testing of the piping job shall be conducted at pressure mentioned in specification for a period of 4 hours by using de-mineralised water, to check its strength. No visible leakages shall be detected during the test. Testing shall be conducted as per tender specification. | Item152
153 | Preparation of final bill of material based on piping GADs. | Item153
154 | Preparation of isometric and fabrication drawings. | Item154
155 | Carrying out Non-destructive testing as required | Item155
156 | Painting of entire system (including aboveground all pipes fittings, flanges and accessories) as per specifications suitable for highly corrosive area environment including supply of approved paints and primers, application of primer and paints, indentification lettering/ numbering, colour coding, etc. as specified including rub down & touch up of shop primer or scrapping of shop primer wherever required by COMPANY and providing scaffolding for all heights etc. | Item156
157 | Cleaning and flushing by water/ compressed air, testing of the systems including hydrostatic, pneumatic and any other type of testing as specified, draining, drying by compressed air/other methods approved by COMPANY. | Item157
158 | Precommissioning & making operational all piping system and equipments. | Item158 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
159 | Commissioning Contractor scope shall provide all necessary assistance in term of supply of man-power, equipment, tools and tackles required amount of nitrogen for purging of entire terminal piping system including equipments etc. to the company during commissioning activities. | Item159 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
160 | Completion of all such work in all respects as per scope of work and as per drawings, specifications and instructions of the COMPANY and keeping the system ready in all respects for further commissioning and start up. | Item160 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
161 | Hook-up works (with client/ consumer piping at battery limits): | Item161 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
162 | Complete Carbon Steel aboveground Piping Work with painting including all fittings, flanges and supply of all required gaskets, studs bolts & nuts etc. and Any other work and material required for the completion of the work and not covered above and desired by EIC shall be in the scope of contractor | Item162 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
163 | Carbon Steel Pipe (ASTM A 106, Seamless B-36.10 / API X 52) | Item163 | 150 | inch Dia |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
164 | 1) Pipe Specification and thickness may vary depending upon availability of pipe. No extra payment shall be made for this. 2) All butt welded fittings & flanges end shall generally match with connecting pipe wall thickness. However, in case of misalignment, Contractor shall have to do end preparation without any extra cost. 3) All o-lets less than 2" NB size, all sizes of coupling and nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under erection rate. | Item164 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
165 | Aboveground installation of Insulating Joint & Valves etc. Handling including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site and installation of all types of valves, insulating joint including assembly of valve accessories, (if any) by bolting, threading or welding, supply and insertion of gaskets, nuts & bolts, nipples, etc. at all elevations of pipe sleepers, supports or overhead on racks, equipments nozzle, skid & painting etc. supply of all consumables, manpower, equipment, etc. for completion of all works as per scope of work and as per drawings, specifications and instructions of Engineer-in-charge including servicing/ cleaning of valve wherever requried. | Item165 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
166 | 12" NB, 300# - Insulating Joints | Item166 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
167 | STRUCTURAL WORKS | Item167 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
168 | Supply of erection of single leaf mild steel gate 2.5m high with mesh upto 2m height and barbed wire fencing and 2m wide complete in all respect including painting as per TS on all MS items, all works as per specification and drawings excluding foundations and RCC beams. | Item168 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
169 | Supply of all materials, fabrication and erection of chain link fencing 2.5m high with mesh up to 2m height and barbed wire fenching complete in all respects including painting as per TS on all MS items, all works as per specification and drawings excluding foundation and RCC beams. | Item169 | 200 | RM |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
170 | Pipe Supports & Other Structures | Item170 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
171 | Supply, fabrication and erection of all types of pipe supports like clamps, saddle, guide stops, cradles, turn buckles, anchors, T-posts; stockade/ trestle and pipe bridge for overhead piping; frames for canopy, approach ladders and platforms, crossover, cable tray supports, etc. including painting suitable for highly corrosive area as per specification labour and supervision & complete work as per drawings, specifications and instruction of Engineerqw-incharge. (Bolts, nuts, washers, U-clamps etc. for supporting shall be supplied by the Contractor within the rates quoted. These items will not be measured and paid seperately). The work is to be completed in all respect as per scope of work and specification. | Item171 | 200 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
172 | Notes: | Item172 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
173 | The quantities indicated are estimated values and hence are approximate. Final payment will be made based on actual quantities to be certified by the Purchaser. | Item173
174 | The cost of MS bolts (permanent and service(, washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants etc., as required for the work shall be deemed to be included in the quoted rates. | Item174 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
175 | All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accrodance with time schedule, are deemed be included in the quoted rates. | Item175
176 | CIVIL WORKS | Item176
177 | Site Grading Excavation in earth and filling to the grades and levels shown in the approved drawings in all kinds of conditions including for Road embarkments, using approved quality good earth from designated borrow area, for all heights and depths including clearing and stripping (min. 150mm) of the area marked for filling, taking spot levels, consolidating the exposed natural soil surface, excavating the earth from borrow area loading, transporting & unloading, spreading in layers not exceeding 150mm thickness, breaking clods, watering (if reqd.), ramming and compacting by manual/ mechanical means to give minimum 92% of modified Proctor's density of earth, testing & dressing including disposal of all unserviceable material all complete as per specifications and directions of Engineer-in-charge. | Item177 | 300 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
178 | (Rate to include cost of all labour, tools, tackles, equipment, hire charges, cost of borrow earth by way of royalties, right of way, cess etc., as applicable with all bye works and sundry works). | Item178
179 | Plain Cement Concrete Supplying and laying plain cement concrete (including shuttering of required) in all types of concrete works including levelling courses below foundation, substructure, superstrcuture, chambers, cable tranch, under floors and any other locations, at all leveies as per drawings, specifications and directions of the Engineer-in-charge. | Item179
180 | PCC 1:2:4 1 Cement : 2 Coarse sand : 4 stone aggregate 20mm nominal size. | Item180 | 500 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
181 | Reinforced Cement Concrete Providing and laying reinforced cement of grade M-20 with 20mm and down grade crushed stone aggregate in all types of structures like foundations, pedestals, pedestal bases, pipe supports, sleepers cable trench inlcuding constrcution joints, bitumen painting on surface in contact with soil, providing and fixing reinforcing steel, shuttering, inserts, finishes etc. at all depths and heights complete as per drawings, specifications and direction of the Engineer-incharge. | Item181 | 400 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
182 | Rate to include cost of all labour, tools, tackles, equipment, hire charges, supply of all maerials such as minimum 43 grade cement including sulphate resistant cement for substructures, R/F steel, Inserts, bolts, conduits, bitumen, other minor constrcution materials, shuttering, stanging, earthwork in excavation and backfilling using serviceable earth in all conditions, shorting bailing and pumping out water, testing of concrete, curing etc. with all bye works and syndry works. | Item182
183 | TEMPORARY CATHODIC PROTECTION SYSTEM | Item183
184 | Design, detailed engineering, supply, installation, testing and commissioning of the temporary Cathodic protection system using Mg/ Zn galvanic anodes to protect the external surface of 3 LPE coated entire 5.5 km (approx.) long steel pipeline network against corrosion for design life of minimum 1 year or till commissioning of PCP system whichever is later as per standard specification No. MNGL/Steel/TS/15 for temporary cathodic protection system. Scope shall also include but not limited to the following for completion of jobs: | Item184 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
185 | Measurement of soil resistivity along the right of way of the main pipeline route as per specification for design & installation of anodes. | Item185
186 | Collection of additional data related to cathodic protection along the right of way of pipeline as per specifications. | Item186 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
187 | Supply, installation, testing & commissioning of one set of spark gap arrestor with 2 plate Zinc grounding cell of 20 kg net weight each across each insulating joint as per specification. | Item187
188 | Supply, installation, testing & commissioning one set of polarisation cell with zinc anode at all high tension (66KV or higher) electrical power transmission line/Equipment crossing or running parallel to the pipeline for grounding purpose as per specification. The rating shall depend upon anticipated fault current & ground bed resistance at the location of installation. However, the rating of polarisation cell (krick) shall not be less than 5 KA & number of 20 kg net weight zinc anode shall not be less than two. | Item188
189 | Supply & installation of Zinc Ribbon Anodes at 4-8 O’Clock position in the interval of 2 metre (max.) on carrier pipes at all cased crossings i.e. railways/ roads etc. | Item189 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
190 | Monitoring of the protection system for 6 months. | Item190
191 | All civil/ structural works related to TCP system including supply of bricks, cement & steel etc. required for completion of the system. | Item191 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
192 | For 12" | Item192 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
193 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item193 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
194 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item194 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
195 | FIELD INSTRUMENTATION | Item195 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
196 | PRESSURE INSTRUMENTS | Item196
197 | Supply , Installation of Pressure Gagues and their accessories inclusive of supply of necessary piping materials and tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/ manifolds & hydraulic testing (exclusive of calibration of instruments) as per installation standard attached elsewhere in Tender Document and Supply as per Data Sheet No.MEC/23K8/05/E5/I/001/DS-PG. Give breakup of supply and Installation rate. | Item197 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
198 | CALIBRATION | Item198
199 | Calibration of the instruments listed below including removal of instruments from pre-installed locations like panels, enclosure racks, fields etc. and refixing them back in respective/ required places, providing equipments, necessary test jigs, instrument air and all consumables. Calibration reports shall be prepared and to be submitted to the Purchaser/ Consultant. | Item199
200 | Pressure Gauges | Item200 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
201 | Note: | Item201 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
202 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item202 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
203 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item203 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
204 | PIPING WORKS FOR SECTIONALISING VALVE STATION-CUM-TAP-OFF POINT All works for fabriaction and installation of all piping above ground at all elevations and below ground at all depth for Sectionalising Valve Station alongwith preparation of construction drawings duly approved by EIC, in all type of terrains and soils including transportation and handling of all Owner supplied materials i.e. extended stem butt welded sectionalising gas actuated ball valve, other types of valves, line pipes for mainline, 4" NB pipe for all branch line including ventlines from Owner's designated place(s) of issue to work site. | Item204 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
205 | Contractor shall supply all required size & type of piping material like pipes, fittings & flanges etc. as per PMS alongwith 2" NB pipe for all branch line & vent line (wherever required) including supply of all consumables, manpower, machinaries, materials etc. and carrying out all mechanical works of underground and above ground piping including fabrication, welding, nondestructive testing of welds, weld repairs/ retesting, cleaning/ flushing, pre-hydrotesting & hydrostatic testing, dewatering, functional testing, cutting of mainline and bevelling (if required) | Item205
206 | assembly, including radiography of tie-in joints, corrosion, coating and external painting as required, installation of instruments like pressure/ temperature instruments/ gauges alongwith complete SS Tubing works including supply of SS Tube and thier accessories etc., as required, obtaining all statutory clearances, approvals and permissions for the works (wherever required), making of valve pit (for detail refer relevant drawings) for SV Stationscum- tap-off points enclosed with tender filled with sand, excavation and filling in all types of soils including soft/ hard rock for installation of piping/ pipe supports providing pipe supports, area fencing and gate including all associated civil and structural works; painting, finishing, clean-up and restoration of site; preparation of as-built drawings, documents and project records and performing all works as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge. In this item, instead of Brick Work RCC will be done | Item206 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
207 | Type - I SV Station on 12" Pipeline | Item207 | 1 | Lumpsum for each |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
208 | Note: i) Work under above items are exclusive of all works associated with main pipeline covered under Item No. 1.0 above. ii) All civil/ structural works including area fencing and gate, valve pits except for piping support will be paid separately as per unit rate provided elsewhere in the SOR. iii) All coupling, nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under above item rate. | Item208 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
Total in Figures | [51 empty] | 0 | 0 | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## BoQ8 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR | [49 empty] | 1
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Maharastra Natural Gas Ltd.,Pune
Name of Work: TENDER FOR LAYING & CONSTRUCTION OF 12” NB X 6 KM U/G STEEL PIPELINE NETWORK & ASSOCIATED WORKS FROM NEAR BAN VILLAGE ROAD, BAN TO NEAR USWAD VILLAGE ON MANTHA ROAD .(Section No-08)
Tender No: MNGL/CP/2024-25/109
Do you want to quote for this sheet ? |  |  | Yes
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE / SCHEDULE OF RATES (SOR) (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Rate inclusive of all taxes and duties except Goods & Service Tax (Rs.) | Per Unit Goods & Service Tax (GST) In % (To be entered by the Bidder) | GST in Rs. | Unit rate inclusive of all taxes & duties including GST (Rs.) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | CARBON STEEL PIPES | Item1
2 | PIPELINE LAYING / INSTALLATION in all type of surface (Normal/built-up surface) "Receiving and taking over" as defined in the specifications, handing, loading, transportation and unloading of Owner supplied 3-Layer PE coated linepipes from Owner's designated stack-yard to Contractor's stock yard/workshop/work-site including preliminary activities, preparation of drawings, wherever required for crossing etc. including handling, stacking, stringing on the pipeline Right-of-Use/ pipeline route alignment, carrying out inspection of company supplied materials including linepipes at the time of taking over, laying/ installation of coated linepipes, associated burried valves, barred tees, insulating joints, flanges & fittings of all sizes, thickness & ANSI class rating and accessories as per specification wherever required depending on site condition including execution of all works, "taking over", handling , including loading and unloading, transportation of Owner supplied materials other than linepipe from Owner's designated place (s) of issue to work site, | Item2 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3 | additional lands required for Contractor's storage, fabrication, access for construction, procurement and supply of all materials (except Owner supplied materials), consumables, equipment, labour and other inputs, carrying out all temporary, ancillary, auxiliary works, aquistion of ROU/ROW for laying of pipeline from HDD Exit and entry point to Tie in Point of existing Pipeline/ ROU, ready for commissioning of pipeline as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge, including but not limited to carrying out the following works: | Item3 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4 | Surveying of route and detours required at the time of execution including marking the same in topographical sheet, preparation of construction drawings showing survey details, and submit same to Owner for review / approval. | Item4
5 | Staking and installation of construction markers, clearing, fencing, grubbing, cutting of trees, full filling all the requirements of various statutory/ environment authorities to the entire satisfaction of concerned authorities, grading of work area. Shifting of all obstruction within the ROU/ Pipeline route alignment viz. electrical lines/ poles, telephone line / poles, etc. coordination with concerned authorities and obtain permissions from these authorities. | Item5
6 | Trenching to all depths by excavation in all types of soils including soft/ hard rock and different type of pavement / footpath / roads etc. including rock breaking, chiselling or otherwise cutting etc. as required and storing excavated soil, reusable materials at designated area as directed by Engineer in charge and to a width to accommodate the Steel pipeline as per the relevant standard/ specification etc. [The minimum depth of the top of pipeline shall be 1.2m measured from top of pipeline coating to the top of undisturbed surface of the soil or as per SCC/ OISD - 141 / 226, whichever is higher]. Dewater of trenches if required as per site condition. | Item6
7 | Carrying out repairs of pipe defects/ replacement in case of irreparable defects and repairs of defects of pipe coating not attributable to Owner including defects/ damages occurring during transportation / handling. | Item7
8 | Stringing of line pipes along pipeline trench / ROU on straw / sand / soft soil bags including supply of bags and its filling materials. | Item8
9 | Checking, cleaning, aligning, bending, cutting and bevelling (as required) of pipes for welding and field adjustments including pipe fittings, welding, carrying out non-destructive testing of welds as required including 100% radiography by X-ray and providing all requisite equipment, labour, supervision, materials, films, consumables, all facilities and personnel to process, develop, examine and interpret radiographs and other tests as required, carrying out repairs of weld joints found defective by Engineer-in-Charge, carrying out re-radiography and other tests as required on repaired joints. | Item9
10 | Carrying out installation of carrier line pipe at all minor crossing viz. carttrack, pathway, water bodies etc. at designated depth by open cut (except at crossing by HDD method). | Item10
11 | Carrying out installation of carrier line pipe in the casing pipe at cased crossing (excluding installation of casing pipes which is covered separately). | Item11
12 | Coating of field weld joints, long radius bends (R=3D), elbows, buried fittings and valves etc. including supply of coating materials etc. (i.e. heat shrinkable sleeves and high build epoxy etc.) as per PJS & Technical Specification compatible with 3 layer PE coating material of the line pipe. | Item12 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
13 | Counting the number and type of trees cut in presence of DFO/concerned authorities and keeping record thereof, stacking and handing over of all cut tress. | Item13
14 | Installation / lowering the pipeline in trench to required depth as per PJS, Techanical Specification & drawings, supply & placement of 1.0mm thk. HDPE Yellow colour warning mat,RCC tiles (300 mm width x 50 mm thick) over the pipeline in same trench along the complete route as per standard drawings, data sheets & technical specifications, padding around pipeline as per Standard Drg. no. MNGL/Plng./Steel/03 with suitable soil duly approved by EIC including supply of padding material, backfilling and its compaction to the satisfaction of concerned authorities with excavated earth / borrowed select soil including supply of borrowed select soil duly approved by EIC before backfilling and make ready for restoration to be done by Onwer / concerned authorities. | Item14
15 | Supply and installation of slope breakers, wherever required or, as directed by Onwer / Engineer–in–charge. | Item15
16 | Crossing the all-foreign pipeline / HT line / cable / any other utilities etc. with necessary concrete / HDPE sheet protection including coordination with all agencies and obtaining NOC | Item16
17 | Supply and installation of bank protection alongwith backfill materials duly approved by EIC for pipeline trench and banks falls under minor water body crossing as per technical specification & Std. Drg. No. MNGL/Plng./Steel/28, wherever required or, as directed by Onwer / EIC. | Item17
18 | Training and diversions of streams in steep slope area, wherever required. | Item18
19 | Carrying out air cleaning, pigging, flushing, cleaning and hydrostatic testing of complete pipeline with required quantity of corrosion inhibitor including pre-testing of designated sections complete as per specification and approved by Engineer–in–charge to specified pressures indicated elsewhere and duration after stabilization as per specification, providing all equipment, pumps, fittings, instruments, dead weight tester, pressure recorder, thermocouples etc., and services, supervision, labour, consumables, water including supply of corrosion inhibitor, air, etc. as required, locating of leaks and rectification of defect attributable to Contractor (rectification of defects in linepipe material not attributable to contractor shall be paid separately as per other item of schedule of rate), re-testing after rectification, dewatering after successful completion of hydrotesting of entire section and as per specification | Item19
20 | All tieing-in, including the tie-in(s) of the pipeline with the adjacent sections of pipeline including cutting of test header, rebevelling as required, radiography and other NDT examination, joint coating as per specification. | Item20
21 | Final clean-up of right-of-use or area disturbed by contractor during their construction activities for laying of pipeline works and disposal of debris and surplus material to designated disposal areas and backfilling of trench and compaction of the same as per satisfaction of Owner and / Or as directed by Engineer–in–charge. | Item21
22 | Installation of all burried valves (except extended stem valves) inside the valve pit and making provision to operate the valve. | Item22 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
23 | Preparation of as-built drawings, pipe-books (1 set of tracing on polyester film and 6 sets of as-built drawings and 1 soft copy and 6 hard copies of pipe book) All the works shall be executed in accordance with the provision of contract including carrying out all temporary/ ancillary/ auxiliary works required for the performance of the works and all other acts, deeds, matters and things necessary to make the pipeline ready for precommissioning activities. | Item23 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
24 | Raking up of hard surface of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. Payment for cutting of hard rock, if any, is covered unders SOR no. 76 | Item24 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
25 | Specified dia Thk (mm) Material Coating Type Length of each pipe (mm) NB | Item25 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
26 | 305 (approx.) 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item26 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
27 | Note: This item shall be applicable for the underground steel grid main pipeline & branch pipeline, barred tees, insulating joints, bends, flanges & fittings, accessories etc. (i.e. including arrangement for making provision for tap-off on proposed steel grid main pipeline) and aboveground approach pipeline upto Insulating Joint (excluding installation of aboveground insulating joint) for various stations. | Item27
28 | Items except above are covered separately. The lengths of pipelines are tentative. | Item28 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
29 | Permission Liasioning /Follow-up | Item29 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
30 | Liasioning & follow up for Permission with all the concerned authorities & boards viz Railways, NH, PWD, MIDC, Local Municipal, Panchyat, Electricity, REC, RES, Sewage water, Drinking water, Forest, Social Forestry, Owners of OFC, Traffic, Law & Order, Fire Brigade, Private Land Owner etc. for entire pipeline length and associated terminals (like SVs, tap-offs) alongwith associated work as per tender. | Item30 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
31 | Laying of RCC Tiles | Item31 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
32 | Providing single layer of RCC Tiles with supply of RCC Tiles to entire width of trench above Warning Mat placed in trench over the laid pipeline as per standard drawing, specification and instruction of Owner. (Rate to include cost of all labour, tools, tackles, equipment, hire charges & supply of all materials, etc.) | Item32
33 | For width of 12" pipeline trench | Item33 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
34 | Barricading to comply with HSSE | Item34 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
35 | Steel barricading of the trenches Cautionary Sign Boards and lighting arrangement shall be provided as per attched drawing no.MNGL/Plng./steel/04. The rates include barricading of trenches along with sign boards, lighting etc. and maintain the same till the back filling of the trench. Rates will be payable per metre of BARRICADING PROVIDED. If proper barricading is not provided, MNGL will barricade the trenches at the risks and costs of the CONTRACTOR and will levy penalty of twice the rate per unit for the relevant section of the pipeline apart from other actions as per contract. | Item35 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
36 | RESTORATION OF ROADS Restoration of asphalt / concrete / red stone roads / pavement/Footpath/Paver block including compaction of soil, to original condition as per requirement and to the entire satisfaction of EIC and / or concerned Owners having jurisdiction for following thickness. | Item36 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
37 | Restoration of Asphalt road upto 10 cm thickness | Item37 | 800 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
38 | Restoration of Asphalt road beyond 10 cm upto 20 cm thickness | Item38 | 300 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
39 | Restoration of Concrete road upto 10 cm thickness | Item39 | 700 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
40 | Restoration of red stone road / footpath / pavement/ Paverblock upto 4 cm thickness | Item40 | 700 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
41 | BORROWED SELECT SOIL FOR BACKFILLING Additional work over and above item 1.0 for supply of specified and approved quality of borrowed soft graded soil / sand in place of available excavated material and / or other suitable soil as per applicable standards / specifications, including backfilling of excavated trench for specified length after laying and padding of pipeline, including transportation of such special backfill material over all distances, complete. | Item41 | 900 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
42 | CROSSING OF STEEL PIPELINE BY OPEN CUT | Item42
43 | Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insatllation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed. | Item43
44 | Road Crossing By Open Cut Method Road Crossings at various locations by Open cut Method as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item44 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
45 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method | Item45 | 90 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
46 | Water body Crossing By Open Cut Method water/ canal/ nallah/ drain/ channel Crossings at various locations by Open cut Method if necessary as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item46 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
47 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method | Item47 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
48 | Note: Laying of the pipeline by the approved method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item48
49 | Backfilling of the Road/water/ canal/ nallah/ drain/ channel Crossings/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority. | Item49
50 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item50 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
51 | CROSSINGS/LAYING ALONG THE ROAD BY HDD METHOD | Item51
52 | Complete work of the any crossing (between the limits are defined as approved drawings) by HDD method including "Receiving and taking over" owner supplied three layer PE coated line pipes from Owner's designated place to issue/ dump site(s) and transportation to Contractor's stock yard/ work shop/ work site including all handling loading, unloading, aligning etc. supply of all Contractor supplied material, manpower, equipment, other resources and aquiring the required land for storage, fabrication inclduing string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type Heat Shrink Sleeve and repair of pipeline coating with special repair patch materials as per specification,pre-testing etc. of complete string made for crossing access for Contractor etc and execution of, but not limited to, following works in accordance with specifications scope of work and instructions of Engineer-in-charge and as per all provision of Contract Document. | Item52
53 | Pre-construction surveys based on site visit, collection of historical data from irrigation/ concerned department including design & calculation and detail engineering and making of crossing drawing for getting their approval from concerned Authority/ Engineer-in-charge, getting work permit/ NOC for water crossings/ road crossings as well as utility crossings (if any) encountered during crossing prior to start the execution of work. | Item53 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
54 | Directional drilling to required depth from top of road including maintenance of drill hole in all types of strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) at all depth to accommodate the pipeline at all conditions encountered during rail/ road crossing by approved HDD methods for providing minimum cover specified in code/ specification or the actual depth as decided by concerned authority, whichever is more. | Item54 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
55 | In case of water crossing, drilling to the required depth on the banks and bed including maintenance of drill hole in all types of soil strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) all depth to accommodate the pipeline a by HDD methods for providing with minimum cover over top of the pipe at all point across the maximum possible width of water bed (as per drawing) either 1.5 mtrs. below the predicted scour profile expected during the life time of the pipeline or 2.5 mtrs. below the available lowest firm bed (if scour profile/ depth not available) of the water crossing by ascertaining bed level upto 50 mtrs. both the side from crossing location or the actual depth as decided by concerned Authority/ Engineer-in-charge whichever is more. | Item55 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
56 | Laying of the pipeline by the approved HDD method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints with special type Dirax Heat Shrink Sleeve or equivalent and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item56 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
57 | Backfilling of the ditch/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority and all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specification, approved drawings, calculations, methods and to the satisfaction of Engineer-in-charge and/or as directed by concerned Authority. | Item57 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
58 | Post installation hydrotest dewatering and tie-in with pipeline at either side of crossing/banks etc. | Item58 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
59 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item59 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
60 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 by HDD Method . | Item60 | 450 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
61 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item61 | 150 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
62 | Installation of carrier pipes by rock drilling for Road/water/Canal/ nallah/ drain/ channel/along the road, or wherever required in all types of hard rock. It includes survey of the underground utilities, submission of profile for approval, execution of the work as per the standard procedure, including , excavation of the pits, insertion/pulling of the carrier pipe, removal of malba, subsequent backfilling and restoration of the facility crossed as per original condition, including supply of all other materials, equipment, consumables, manpower etc including string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type of Heat Shrink Sleeve (Direx) and repair of pipeline coating with special repair patch materials as per Specification, pre-testing etc. of complete string made for crossing/ laying access for Contractor etc. and execution of, but not limited to, following works in accordance with specifications and instruction of Engineer-in-Charge and as per all provision of Contract Document. Balance activities as defined in SOR Item of open trench. Note:The length of HDD mentioned is tentative and may vary to the considerable extent depending upon requirements as per site conditions. The length mentioned in SOR is indicative for all the crossing to be done by HDD, numbers and locations shall be decided by Engineer-in-Charge depending upon site condition. Payment for the length of final tie-in carrier pipeline string with mainline laid by HDD are inclusive in this above item rate. No separate payment shall be made under other clauses mentioned elsewhere. Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item62
63 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 by HDD method | Item63 | 400 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
64 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item64 | 120 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
65 | Note: (i) Crossing width & Actual string length for HDD shall vary as per design calculations & site condition so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. | Item65
66 | (ii)Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item66
67 | (iii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by HDD method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item67
68 | (iv) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossing at different locations. | Item68
69 | (v) The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. | Item69
70 | Note: (i) Quantity mentioned under item nos. 44, 46 are indicative only for different location of roads/water/ canal/ nallah/ drain/ channel Crossings. (ii) Actual length & width of individual crossing and cover from top of casing pipe/ carrier pipe string may vary depending upon site condition, approved crossing drawings, specifications etc. and / or as decided by Engineer-in-charge/ Concerned Authority. | Item70
71 | (iii) Payment for supply & installation of Zinc ribbon anode and its design excluded from above item and covered elsewhere in the SOR. (iv) Payment for the length carrier pipeline string inserted in casing pipe laid by Boring are covered separately and shall be paid under other clauses mentioned elesewhere in the SOR. | Item71
72 | Excavation beyond 1.5m depth in case of crossing of utilities/ drain/ culverts etc. through open cut upto the following depth (including restoration of the damaged area to its original condition and satisfaction of the Engineer-in-charge / concerned authorities) : - | Item72 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
73 | In all type of surface (Kachha/ built-up surface / Hard surface) of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. The other activities are as per SOR 1.1. Payment for cutting of hard rock, if any, is covered unders SOR no. 76 | Item73
74 | Deeper than 1.5 m & upto 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item74 | 600 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
75 | Deeper than 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item75 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
76 | Excavation of hard rock | Item76
77 | Excavation of hard rock wherever hard rock of single piece exceeding 1.0 m in length removable by pneumatic chisel/ drill as per direction of EIC. | Item77 | 3800 | Cub. M |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
78 | REPAIR OF COATING DEFECTS (NOT ATTRIBUTED TO CONTRACTOR) | Item78
79 | Repair of Holiday in Coating (Noted and recorded at the time of "receiving and taking over") Supply of all coating repair materials as per requirements of specification to be compatible with line pipe coating material, supply of all consumables, utilities, equipments and all manpower required, pipe cleaning and surface preparation, repairing of coating defects (resulting in holiday) and testing including all handling, transportation, etc. for line pipes, performing all works necessary for the completion of the works stirctly in accordance with relevant specification and instructions of Engineer-In-Charge. This rate shall be applicable per sq. cm of the exposed steel area exposed steel area. | Item79 | 2200 | Sq. cm. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
80 | PERMANENT MARKERS Supply, fabrication and installation of all types of permanent markers along the route including all associated civil works such as excavation in all types of soil, construction in all types of soil, construction of pedestals and grouting with concrete, clearing, supply and application of approved colour and quality of primer and paint, stencil letter cutting for numbers, direction, change etc., restoration of area to original condition and performing all works as per drawing, specification and instruction of engineer-in-charge. | Item80
81 | Pipeline RCC boundary / route marker as per drawing | Item81 | 120 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
82 | Pipeline warning markers with post & foundations | Item82 | 40 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
83 | Pipeline direction marker with post & foundations | Item83 | 25 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
84 | Pipeline KM with post & foundations | Item84 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
85 | HOOK -UP | Item85
86 | Hook-up of proposed pipeline by welding of final tie-in-joint with any existing laid pipeline portion of river X-ing ,existing Tap-off & battery limit of section IV including Hook-up point of the existing pipeline to be made ready for welding by cutting of flanges / valves / headers at all depth in all type of soil etc. Venting of N2 / gas / gas mixture as required purging of N2 Gas (if required), rebevelling as required, radiography and other NDT examination, joint coating as per specification.Contractor shall supply of all consumables, manpower, machinaries, materials, N2 gas etc. and carry out all works as per the provisions of Contract document and instructions of Engineer-in-charge. | Item86
87 | For 12" NB | Item87 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
88 | PRE-COMMISSIONING AND ASSISTANCE IN COMMISSIONING OF PIPELINE SYSTEM Swabbing, drying, purging with nitrogen of the complete pipeline network and the associated facilities being installed to the specified acceptance criteria, carrying out pre-commissioning works, providing assistance during the complete duration of commissioning operations for entire pipeline network system including supply of all equipment, man-power, consumables (including pigs & nitrogen required for purging with maintaining nitrogen column of mininum 10% of pipeline geometric volume) materials for all temporary works and performing all associated works, complete as per the relevant specifications, other provisions of Contract document and instructions of Engineer-in-charge. | Item88
89 | For 12" NB Pipeline | Item89 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
90 | IDLE TIME PRESERVATION OF PIPELINE Preservation of complete pipeline and associated facilities forming part of the pipeline as per Bid document and its maintenance including supply of all consumables, all equipment, manpower, etc. complete as per the requirements of specifications, other provisions of Contract document and instructions of Engineer-in-charge. Note : Owner reserves the right to exercise either or none of the rates below. | Item90
91 | By filling and pressurizing with nitrogen to a pressure of 2 bar(g) for a period of 3 months. | Item91 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
92 | For 12" NB Pipeline | Item92 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
93 | For every additional period of one month or part thereof | Item93 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
94 | For 12" NB Pipeline | Item94 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
95 | RCC VALVE PITS All civil works including supply of all materials, excavation of pit, piping supports including all PCC and RCC works for valves pits including pedestals with insert plates as required sealing of pipe at valve pits, providing cover etc. and finishing , clean-up and restoration of site, filling and grading of area around valve station for avoiding any local flooding of area, as per typical drawing and specification enclosed and instructions of Engineer-in-charge. In this item, instead of Brick Work, RCC will be done | Item95 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
96 | Valve Pit of Size 2m x 2m | Item96 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
97 | SUPPLY OF ASSORTED PIPE, FITTINGS AND FLANGES Complete works of supply of pipes, flanges & fittings for aboveground & underground installation including all taxes, duties, transportation and inspection charges but not limited to, the following items in accordance with PMS (piping material specification), relevant specifications & drawings indicated in job specification under SCC (technical) and instructions of Engineer-in-charge and as per all provisions of the CONTRACT DOCUMENT. - Handling including lifting, transportation from Contractor Stores to CONTRACTOR's workshop for fabrication and/ or to work site for field fabrication and erection for all piping items supplied by Contractor. | Item97
98 | Carbon Steel Pipe (A 106, Seamless B-36.10/ API X 52 ) | Item98
99 | Size Rating/ Schedule | Item99 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
100 | 2" NB, BE Sch. 80 | Item100 | 60 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
101 | 1" NB, PE Sch. 80 | Item101 | 42 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
102 | ¾" NB, PE Sch. 160 | Item102 | 40 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
103 | Flanges | Item103
104 | Weld Neck (B-16.5, 300# A105,125 AARH, Serrated finish) | Item104
105 | Size Rating/ Schedule | Item105 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
106 | 2" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item106 | 10 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
107 | Blind Flanges (B-16.5, 300# A105,125 AARH Serrated) | Item107
108 | Size | Item108
109 | 2" NB, RF | Item109 | 10 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
110 | Elbow (Seamless) | Item110 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
111 | 90° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item111
112 | Size Rating/ Schedule | Item112
113 | 12" NB 300# | Item113 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
114 | 45° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item114 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
115 | Size Rating/ Schedule | Item115
116 | 12" NB 300# | Item116 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
117 | 90° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item117 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
118 | Size Rating/ Schedule | Item118
119 | 12" NB 300# | Item119 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
120 | 45° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item120
121 | Size Rating/ Schedule | Item121
122 | 12" NB 300# | Item122 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
123 | 22½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D) Min Thickness 6.4mm | Item123 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
124 | Size Rating/ Schedule | Item124
125 | 12" NB Sch. Std. | Item125 | 16 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
126 | 11½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D), Min Thickness 6.4mm | Item126
127 | Size Rating/ Schedule | Item127
128 | 12" NB 300# | Item128 | 16 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
129 | Tees (Seamless) | Item129
130 | Equal Tee (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item130
131 | Size Rating/ Schedule | Item131
132 | 12" NB x 12" NB x 12" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item132 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
133 | 2" NB x 2" NB x 2" NB Sch. XS | Item133 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
134 | Weldolet and Sockolet | Item134
135 | Weldolet (MOC A105 & DIM. MSS SP 97) | Item135
136 | Size Rating/ Schedule | Item136
137 | 12" NB x 2" NB Sch. 80. | Item137 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
138 | Sockolet (MOC A105 & DIM. MSS SP 97) | Item138
139 | 12" NB x 3/4" NB #6000 | Item139 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
140 | Butt Weld Disc End Cap (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item140
141 | Size Rating/ Schedule | Item141
142 | 12" Sch. Std. | Item142 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
143 | Fabrication & Installation of Underground Valve Assembly | Item143 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
144 | 12"NB Isolation Valve/tap-off assembly as per Drg. No. MNGL/Plng./Steel/40 | Item144 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
145 | Note: | Item145 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
146 | For all the supply items mentioned above, procurement shall be made as per enclosed Data Sheets and respective technical specification, after due approval of Engineer-in-charge. | Item146
147 | The quantities mentioned above are tentative and quantities for above supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item147
148 | PLANT PIPING (ABOVEGROUND) Fabrication and testing of carbon steel piping and fittings, valves, IJ, including supply of all consumables, equipment, manpower, and other resources and execution of job as per instruction AIC/EIC.Transportation of all piping items from Owner's and/ or Contractor's storage point to work at site/ workshop as applicable, complete work of fabrication, erection, painting, testing of pipes, flanges and fittings and making ready for further Commissioning / Start-up of carbon steel piping of all sizes and ratings including supply of all consumables, equipment, manpower and other resources and execution of, but not limited to, as per all provisions of the CONTRACT DOCUMENT. | Item148 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
149 | Fabrication including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site, cutting, edge preparation, inclusive of grinding the edges of pipes, fittings, flanges, reducers etc. to match with the matching edges of uneven thickness, wherever required, fit-up, welding of pipes and fittings like elbows, tees, reducers, weldolets, sockolets, Valves, IJ etc. flanges, vent and drain point connection, Radiography and NDT of all joints etc, including providing stubin connections, fabricated fittings and reinforcement pads etc., as required. | Item149 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
150 | Erection of pipes of all types and thickness at all elevations, connecting with equipment nozzle, aligning, installation and carrying out connected activities for all types of valves, all online instruments and fittings of all sizes of elbow, reducers, tees, flanges, blind flanges, spectacle blind flanges, branch connection / tapping for pressure gauges, including installation of gaskets and bolts. | Item150 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
151 | Erection including prior cleaning, lifting, placing on pipe sleepers and supports, overhead on racks, skids and at all elevations including installation and carrying out connected activities for all types of valves including supply and fixing of gaskets, studs/ bolts, nuts wherever required for all sizes, levelling, aligning, joining of flanges, blind flanges, connecting with equipment, nozzles, strainers, tie-in with existing piping/facilities, etc. tapping for inline instruments like pressure gauges, thermowells, sample connection, etc. | Item151
152 | Hydro testing of the piping job shall be conducted at pressure mentioned in specification for a period of 4 hours by using de-mineralised water, to check its strength. No visible leakages shall be detected during the test. Testing shall be conducted as per tender specification. | Item152
153 | Preparation of final bill of material based on piping GADs. | Item153
154 | Preparation of isometric and fabrication drawings. | Item154
155 | Carrying out Non-destructive testing as required | Item155
156 | Painting of entire system (including aboveground all pipes fittings, flanges and accessories) as per specifications suitable for highly corrosive area environment including supply of approved paints and primers, application of primer and paints, indentification lettering/ numbering, colour coding, etc. as specified including rub down & touch up of shop primer or scrapping of shop primer wherever required by COMPANY and providing scaffolding for all heights etc. | Item156
157 | Cleaning and flushing by water/ compressed air, testing of the systems including hydrostatic, pneumatic and any other type of testing as specified, draining, drying by compressed air/other methods approved by COMPANY. | Item157
158 | Precommissioning & making operational all piping system and equipments. | Item158 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
159 | Commissioning Contractor scope shall provide all necessary assistance in term of supply of man-power, equipment, tools and tackles required amount of nitrogen for purging of entire terminal piping system including equipments etc. to the company during commissioning activities. | Item159 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
160 | Completion of all such work in all respects as per scope of work and as per drawings, specifications and instructions of the COMPANY and keeping the system ready in all respects for further commissioning and start up. | Item160 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
161 | Hook-up works (with client/ consumer piping at battery limits): | Item161 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
162 | Complete Carbon Steel aboveground Piping Work with painting including all fittings, flanges and supply of all required gaskets, studs bolts & nuts etc. and Any other work and material required for the completion of the work and not covered above and desired by EIC shall be in the scope of contractor | Item162 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
163 | Carbon Steel Pipe (ASTM A 106, Seamless B-36.10 / API X 52) | Item163 | 150 | inch Dia |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
164 | 1) Pipe Specification and thickness may vary depending upon availability of pipe. No extra payment shall be made for this. 2) All butt welded fittings & flanges end shall generally match with connecting pipe wall thickness. However, in case of misalignment, Contractor shall have to do end preparation without any extra cost. 3) All o-lets less than 2" NB size, all sizes of coupling and nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under erection rate. | Item164 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
165 | Aboveground installation of Insulating Joint & Valves etc. Handling including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site and installation of all types of valves, insulating joint including assembly of valve accessories, (if any) by bolting, threading or welding, supply and insertion of gaskets, nuts & bolts, nipples, etc. at all elevations of pipe sleepers, supports or overhead on racks, equipments nozzle, skid & painting etc. supply of all consumables, manpower, equipment, etc. for completion of all works as per scope of work and as per drawings, specifications and instructions of Engineer-in-charge including servicing/ cleaning of valve wherever requried. | Item165 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
166 | 12" NB, 300# - Insulating Joints | Item166 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
167 | STRUCTURAL WORKS | Item167 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
168 | Supply of erection of single leaf mild steel gate 2.5m high with mesh upto 2m height and barbed wire fencing and 2m wide complete in all respect including painting as per TS on all MS items, all works as per specification and drawings excluding foundations and RCC beams. | Item168 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
169 | Supply of all materials, fabrication and erection of chain link fencing 2.5m high with mesh up to 2m height and barbed wire fenching complete in all respects including painting as per TS on all MS items, all works as per specification and drawings excluding foundation and RCC beams. | Item169 | 150 | RM |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
170 | Pipe Supports & Other Structures | Item170 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
171 | Supply, fabrication and erection of all types of pipe supports like clamps, saddle, guide stops, cradles, turn buckles, anchors, T-posts; stockade/ trestle and pipe bridge for overhead piping; frames for canopy, approach ladders and platforms, crossover, cable tray supports, etc. including painting suitable for highly corrosive area as per specification labour and supervision & complete work as per drawings, specifications and instruction of Engineerqw-incharge. (Bolts, nuts, washers, U-clamps etc. for supporting shall be supplied by the Contractor within the rates quoted. These items will not be measured and paid seperately). The work is to be completed in all respect as per scope of work and specification. | Item171 | 250 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
172 | Notes: | Item172 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
173 | The quantities indicated are estimated values and hence are approximate. Final payment will be made based on actual quantities to be certified by the Purchaser. | Item173
174 | The cost of MS bolts (permanent and service(, washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants etc., as required for the work shall be deemed to be included in the quoted rates. | Item174 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
175 | All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accrodance with time schedule, are deemed be included in the quoted rates. | Item175
176 | CIVIL WORKS | Item176
177 | Site Grading Excavation in earth and filling to the grades and levels shown in the approved drawings in all kinds of conditions including for Road embarkments, using approved quality good earth from designated borrow area, for all heights and depths including clearing and stripping (min. 150mm) of the area marked for filling, taking spot levels, consolidating the exposed natural soil surface, excavating the earth from borrow area loading, transporting & unloading, spreading in layers not exceeding 150mm thickness, breaking clods, watering (if reqd.), ramming and compacting by manual/ mechanical means to give minimum 92% of modified Proctor's density of earth, testing & dressing including disposal of all unserviceable material all complete as per specifications and directions of Engineer-in-charge. | Item177 | 150 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
178 | (Rate to include cost of all labour, tools, tackles, equipment, hire charges, cost of borrow earth by way of royalties, right of way, cess etc., as applicable with all bye works and sundry works). | Item178
179 | Plain Cement Concrete Supplying and laying plain cement concrete (including shuttering of required) in all types of concrete works including levelling courses below foundation, substructure, superstrcuture, chambers, cable tranch, under floors and any other locations, at all leveies as per drawings, specifications and directions of the Engineer-in-charge. | Item179
180 | PCC 1:2:4 1 Cement : 2 Coarse sand : 4 stone aggregate 20mm nominal size. | Item180 | 300 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
181 | Reinforced Cement Concrete Providing and laying reinforced cement of grade M-20 with 20mm and down grade crushed stone aggregate in all types of structures like foundations, pedestals, pedestal bases, pipe supports, sleepers cable trench inlcuding constrcution joints, bitumen painting on surface in contact with soil, providing and fixing reinforcing steel, shuttering, inserts, finishes etc. at all depths and heights complete as per drawings, specifications and direction of the Engineer-incharge. | Item181 | 200 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
182 | Rate to include cost of all labour, tools, tackles, equipment, hire charges, supply of all maerials such as minimum 43 grade cement including sulphate resistant cement for substructures, R/F steel, Inserts, bolts, conduits, bitumen, other minor constrcution materials, shuttering, stanging, earthwork in excavation and backfilling using serviceable earth in all conditions, shorting bailing and pumping out water, testing of concrete, curing etc. with all bye works and syndry works. | Item182
183 | TEMPORARY CATHODIC PROTECTION SYSTEM | Item183
184 | Design, detailed engineering, supply, installation, testing and commissioning of the temporary Cathodic protection system using Mg/ Zn galvanic anodes to protect the external surface of 3 LPE coated entire 5.5 km (approx.) long steel pipeline network against corrosion for design life of minimum 1 year or till commissioning of PCP system whichever is later as per standard specification No. MNGL/Steel/TS/15 for temporary cathodic protection system. Scope shall also include but not limited to the following for completion of jobs: | Item184 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
185 | Measurement of soil resistivity along the right of way of the main pipeline route as per specification for design & installation of anodes. | Item185
186 | Collection of additional data related to cathodic protection along the right of way of pipeline as per specifications. | Item186 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
187 | Supply, installation, testing & commissioning of one set of spark gap arrestor with 2 plate Zinc grounding cell of 20 kg net weight each across each insulating joint as per specification. | Item187
188 | Supply, installation, testing & commissioning one set of polarisation cell with zinc anode at all high tension (66KV or higher) electrical power transmission line/Equipment crossing or running parallel to the pipeline for grounding purpose as per specification. The rating shall depend upon anticipated fault current & ground bed resistance at the location of installation. However, the rating of polarisation cell (krick) shall not be less than 5 KA & number of 20 kg net weight zinc anode shall not be less than two. | Item188
189 | Supply & installation of Zinc Ribbon Anodes at 4-8 O’Clock position in the interval of 2 metre (max.) on carrier pipes at all cased crossings i.e. railways/ roads etc. | Item189 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
190 | Monitoring of the protection system for 6 months. | Item190
191 | All civil/ structural works related to TCP system including supply of bricks, cement & steel etc. required for completion of the system. | Item191 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
192 | For 12" | Item192 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
193 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item193 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
194 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item194 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
195 | FIELD INSTRUMENTATION | Item195 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
196 | PRESSURE INSTRUMENTS | Item196
197 | Supply , Installation of Pressure Gagues and their accessories inclusive of supply of necessary piping materials and tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/ manifolds & hydraulic testing (exclusive of calibration of instruments) as per installation standard attached elsewhere in Tender Document and Supply as per Data Sheet No.MEC/23K8/05/E5/I/001/DS-PG. Give breakup of supply and Installation rate. | Item197 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
198 | CALIBRATION | Item198
199 | Calibration of the instruments listed below including removal of instruments from pre-installed locations like panels, enclosure racks, fields etc. and refixing them back in respective/ required places, providing equipments, necessary test jigs, instrument air and all consumables. Calibration reports shall be prepared and to be submitted to the Purchaser/ Consultant. | Item199
200 | Pressure Gauges | Item200 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
201 | Note: | Item201 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
202 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item202 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
203 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item203 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
204 | PIPING WORKS FOR SECTIONALISING VALVE STATION-CUM-TAP-OFF POINT All works for fabriaction and installation of all piping above ground at all elevations and below ground at all depth for Sectionalising Valve Station alongwith preparation of construction drawings duly approved by EIC, in all type of terrains and soils including transportation and handling of all Owner supplied materials i.e. extended stem butt welded sectionalising gas actuated ball valve, other types of valves, line pipes for mainline, 4" NB pipe for all branch line including ventlines from Owner's designated place(s) of issue to work site. | Item204
205 | Contractor shall supply all required size & type of piping material like pipes, fittings & flanges etc. as per PMS alongwith 2" NB pipe for all branch line & vent line (wherever required) including supply of all consumables, manpower, machinaries, materials etc. and carrying out all mechanical works of underground and above ground piping including fabrication, welding, nondestructive testing of welds, weld repairs/ retesting, cleaning/ flushing, pre-hydrotesting & hydrostatic testing, dewatering, functional testing, cutting of mainline and bevelling (if required) | Item205
206 | assembly, including radiography of tie-in joints, corrosion, coating and external painting as required, installation of instruments like pressure/ temperature instruments/ gauges alongwith complete SS Tubing works including supply of SS Tube and thier accessories etc., as required, obtaining all statutory clearances, approvals and permissions for the works (wherever required), making of valve pit (for detail refer relevant drawings) for SV Stationscum- tap-off points enclosed with tender filled with sand, excavation and filling in all types of soils including soft/ hard rock for installation of piping/ pipe supports providing pipe supports, area fencing and gate including all associated civil and structural works; painting, finishing, clean-up and restoration of site; preparation of as-built drawings, documents and project records and performing all works as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge. In this item, instead of Brick Work RCC will be done | Item206
207 | Type - I SV Station on 12" Pipeline | Item207 | 1 | Lumpsum for each |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
208 | Note: i) Work under above items are exclusive of all works associated with main pipeline covered under Item No. 1.0 above. ii) All civil/ structural works including area fencing and gate, valve pits except for piping support will be paid separately as per unit rate provided elsewhere in the SOR. iii) All coupling, nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under above item rate. | Item208
209 | Details of Major Road Crossing (Canal/SH/DR/NHAI): Supply, Installation & Insertion of pipeline across Canal / State Highways as per SCC and technical specifications | Item209 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
210 | Supply & Installation of 24" NB x 6.4mm Wall thk. Casing pipe for Line Pipe 12"NB(6.4 mm thk API 5L Gr X52) by Jacking Boring . Including Insertion of 12" dia Carrier pipeline in 24" dia casing pipe and connectivity with existing pipeline at both end of National Highways/State Highways/ Railway as per SCC and technical specifications -Supply of Casing Pipe Supply of following casing pipe including handling, loading, transportation & unloading etc. to contractor's own stock yard / worksite(s). -After Completion of insertion of carrier pipe with Connectivity at both end including all works as per the scope of work -Post Hydro testing & Commissioning , Submission of as-built drawing, Submission of Documents - The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. | Item210
211 | Note: (i) Crossing width may vary as per site condition. Tenderer are advised to visit site for actual assessment of extent of crossing. Actual length of Boring shall be as per design calculations so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. (ii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by Boring method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item211 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
212 | (iii) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossings at different locations. | Item212 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
213 | (iv) Actual length & cover from top of casing pipe string may vary depending upon site conditions, approved drawings, specification etc. and / or as decided by concerned Authority / Engineer-in-charge. (vi) No Extra Payment for supply & installation of Zinc ribbon to be provided to Carrier pipe & Zinc Anode is to be provided to Casing pipe and its design included in above item | Item213 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
214 | Supply and installation of 24'' casing pipe,Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insertion of carrier pipe in casing pipe after above ground pretesting at specified test pressure and installation of casing insulators & Zinc ribbon anode as per specification/ drawings. Installation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed (Any type of soil) | Item214 | 100 | Mtrs |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
Total in Figures | Gross Total Amount inclusive of all taxes and duties excluding Goods & Service Tax (in figures) | [50 empty] | 0 | 0 | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures | Gross Total Amount inclusive of all taxes and duties including Goods & Service Tax (in figures) |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## BoQ9 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR | [49 empty] | 1
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Maharastra Natural Gas Ltd.,Pune
Name of Work: TENDER FOR LAYING & CONSTRUCTION OF 12” NB X 6 KM U/G STEEL PIPELINE NETWORK & ASSOCIATED WORKS FROM NEAR USWAD VILLAGE ON MANTHA ROAD TO NEAR CHIKHALI VILLAGE ROAD, CHIKHALI (Section No-09)
Tender No: MNGL/CP/2024-25/109
Do you want to quote for this sheet ? |  |  | Yes
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE / SCHEDULE OF RATES (SOR) (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Rate inclusive of all taxes and duties except Goods & Service Tax (Rs.) | Per Unit Goods & Service Tax (GST) In % (To be entered by the Bidder) | GST in Rs. | Unit rate inclusive of all taxes & duties including GST (Rs.) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | CARBON STEEL PIPES | Item1
2 | PIPELINE LAYING / INSTALLATION in all type of surface (Normal/built-up surface) "Receiving and taking over" as defined in the specifications, handing, loading, transportation and unloading of Owner supplied 3-Layer PE coated linepipes from Owner's designated stack-yard to Contractor's stock yard/workshop/work-site including preliminary activities, preparation of drawings, wherever required for crossing etc. including handling, stacking, stringing on the pipeline Right-of-Use/ pipeline route alignment, carrying out inspection of company supplied materials including linepipes at the time of taking over, laying/ installation of coated linepipes, associated burried valves, barred tees, insulating joints, flanges & fittings of all sizes, thickness & ANSI class rating and accessories as per specification wherever required depending on site condition including execution of all works, "taking over", handling , including loading and unloading, transportation of Owner supplied materials other than linepipe from Owner's designated place (s) of issue to work site, | Item2 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3 | additional lands required for Contractor's storage, fabrication, access for construction, procurement and supply of all materials (except Owner supplied materials), consumables, equipment, labour and other inputs, carrying out all temporary, ancillary, auxiliary works, aquistion of ROU/ROW for laying of pipeline from HDD Exit and entry point to Tie in Point of existing Pipeline/ ROU, ready for commissioning of pipeline as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge, including but not limited to carrying out the following works: | Item3 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4 | Surveying of route and detours required at the time of execution including marking the same in topographical sheet, preparation of construction drawings showing survey details, and submit same to Owner for review / approval. | Item4
5 | Staking and installation of construction markers, clearing, fencing, grubbing, cutting of trees, full filling all the requirements of various statutory/ environment authorities to the entire satisfaction of concerned authorities, grading of work area. Shifting of all obstruction within the ROU/ Pipeline route alignment viz. electrical lines/ poles, telephone line / poles, etc. coordination with concerned authorities and obtain permissions from these authorities. | Item5
6 | Trenching to all depths by excavation in all types of soils including soft/ hard rock and different type of pavement / footpath / roads etc. including rock breaking, chiselling or otherwise cutting etc. as required and storing excavated soil, reusable materials at designated area as directed by Engineer in charge and to a width to accommodate the Steel pipeline as per the relevant standard/ specification etc. [The minimum depth of the top of pipeline shall be 1.2m measured from top of pipeline coating to the top of undisturbed surface of the soil or as per SCC/ OISD - 141 / 226, whichever is higher]. Dewater of trenches if required as per site condition. | Item6
7 | Carrying out repairs of pipe defects/ replacement in case of irreparable defects and repairs of defects of pipe coating not attributable to Owner including defects/ damages occurring during transportation / handling. | Item7
8 | Stringing of line pipes along pipeline trench / ROU on straw / sand / soft soil bags including supply of bags and its filling materials. | Item8
9 | Checking, cleaning, aligning, bending, cutting and bevelling (as required) of pipes for welding and field adjustments including pipe fittings, welding, carrying out non-destructive testing of welds as required including 100% radiography by X-ray and providing all requisite equipment, labour, supervision, materials, films, consumables, all facilities and personnel to process, develop, examine and interpret radiographs and other tests as required, carrying out repairs of weld joints found defective by Engineer-in-Charge, carrying out re-radiography and other tests as required on repaired joints. | Item9
10 | Carrying out installation of carrier line pipe at all minor crossing viz. carttrack, pathway, water bodies etc. at designated depth by open cut (except at crossing by HDD method). | Item10
11 | Carrying out installation of carrier line pipe in the casing pipe at cased crossing (excluding installation of casing pipes which is covered separately). | Item11
12 | Coating of field weld joints, long radius bends (R=3D), elbows, buried fittings and valves etc. including supply of coating materials etc. (i.e. heat shrinkable sleeves and high build epoxy etc.) as per PJS & Technical Specification compatible with 3 layer PE coating material of the line pipe. | Item12 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
13 | Counting the number and type of trees cut in presence of DFO/concerned authorities and keeping record thereof, stacking and handing over of all cut tress. | Item13
14 | Installation / lowering the pipeline in trench to required depth as per PJS, Techanical Specification & drawings, supply & placement of 1.0mm thk. HDPE Yellow colour warning mat,RCC tiles (300 mm width x 50 mm thick) over the pipeline in same trench along the complete route as per standard drawings, data sheets & technical specifications, padding around pipeline as per Standard Drg. no. MNGL/Plng./Steel/03 with suitable soil duly approved by EIC including supply of padding material, backfilling and its compaction to the satisfaction of concerned authorities with excavated earth / borrowed select soil including supply of borrowed select soil duly approved by EIC before backfilling and make ready for restoration to be done by Onwer / concerned authorities. | Item14
15 | Supply and installation of slope breakers, wherever required or, as directed by Onwer / Engineer–in–charge. | Item15
16 | Crossing the all-foreign pipeline / HT line / cable / any other utilities etc. with necessary concrete / HDPE sheet protection including coordination with all agencies and obtaining NOC | Item16
17 | Supply and installation of bank protection alongwith backfill materials duly approved by EIC for pipeline trench and banks falls under minor water body crossing as per technical specification & Std. Drg. No. MNGL/Plng./Steel/28, wherever required or, as directed by Onwer / EIC. | Item17
18 | Training and diversions of streams in steep slope area, wherever required. | Item18
19 | Carrying out air cleaning, pigging, flushing, cleaning and hydrostatic testing of complete pipeline with required quantity of corrosion inhibitor including pre-testing of designated sections complete as per specification and approved by Engineer–in–charge to specified pressures indicated elsewhere and duration after stabilization as per specification, providing all equipment, pumps, fittings, instruments, dead weight tester, pressure recorder, thermocouples etc., and services, supervision, labour, consumables, water including supply of corrosion inhibitor, air, etc. as required, locating of leaks and rectification of defect attributable to Contractor (rectification of defects in linepipe material not attributable to contractor shall be paid separately as per other item of schedule of rate), re-testing after rectification, dewatering after successful completion of hydrotesting of entire section and as per specification | Item19
20 | All tieing-in, including the tie-in(s) of the pipeline with the adjacent sections of pipeline including cutting of test header, rebevelling as required, radiography and other NDT examination, joint coating as per specification. | Item20
21 | Final clean-up of right-of-use or area disturbed by contractor during their construction activities for laying of pipeline works and disposal of debris and surplus material to designated disposal areas and backfilling of trench and compaction of the same as per satisfaction of Owner and / Or as directed by Engineer–in–charge. | Item21
22 | Installation of all burried valves (except extended stem valves) inside the valve pit and making provision to operate the valve. | Item22 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
23 | Preparation of as-built drawings, pipe-books (1 set of tracing on polyester film and 6 sets of as-built drawings and 1 soft copy and 6 hard copies of pipe book) All the works shall be executed in accordance with the provision of contract including carrying out all temporary/ ancillary/ auxiliary works required for the performance of the works and all other acts, deeds, matters and things necessary to make the pipeline ready for precommissioning activities. | Item23 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
24 | Raking up of hard surface of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. Payment for cutting of hard rock, if any, is covered unders SOR no. 76 | Item24 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
25 | Specified dia Thk (mm) Material Coating Type Length of each pipe (mm) NB | Item25 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
26 | 305 (approx.) 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item26 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
27 | Note: This item shall be applicable for the underground steel grid main pipeline & branch pipeline, barred tees, insulating joints, bends, flanges & fittings, accessories etc. (i.e. including arrangement for making provision for tap-off on proposed steel grid main pipeline) and aboveground approach pipeline upto Insulating Joint (excluding installation of aboveground insulating joint) for various stations. | Item27
28 | Items except above are covered separately. The lengths of pipelines are tentative. | Item28 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
29 | Permission Liasioning /Follow-up | Item29 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
30 | Liasioning & follow up for Permission with all the concerned authorities & boards viz Railways, NH, PWD, MIDC, Local Municipal, Panchyat, Electricity, REC, RES, Sewage water, Drinking water, Forest, Social Forestry, Owners of OFC, Traffic, Law & Order, Fire Brigade, Private Land Owner etc. for entire pipeline length and associated terminals (like SVs, tap-offs) alongwith associated work as per tender. | Item30 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
31 | Laying of RCC Tiles | Item31 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
32 | Providing single layer of RCC Tiles with supply of RCC Tiles to entire width of trench above Warning Mat placed in trench over the laid pipeline as per standard drawing, specification and instruction of Owner. (Rate to include cost of all labour, tools, tackles, equipment, hire charges & supply of all materials, etc.) | Item32
33 | For width of 12" pipeline trench | Item33 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
34 | Barricading to comply with HSSE | Item34 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
35 | Steel barricading of the trenches Cautionary Sign Boards and lighting arrangement shall be provided as per attched drawing no.MNGL/Plng./steel/04. The rates include barricading of trenches along with sign boards, lighting etc. and maintain the same till the back filling of the trench. Rates will be payable per metre of BARRICADING PROVIDED. If proper barricading is not provided, MNGL will barricade the trenches at the risks and costs of the CONTRACTOR and will levy penalty of twice the rate per unit for the relevant section of the pipeline apart from other actions as per contract. | Item35 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
36 | RESTORATION OF ROADS Restoration of asphalt / concrete / red stone roads / pavement/Footpath/Paver block including compaction of soil, to original condition as per requirement and to the entire satisfaction of EIC and / or concerned Owners having jurisdiction for following thickness. | Item36 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
37 | Restoration of Asphalt road upto 10 cm thickness | Item37 | 800 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
38 | Restoration of Asphalt road beyond 10 cm upto 20 cm thickness | Item38 | 300 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
39 | Restoration of Concrete road upto 10 cm thickness | Item39 | 900 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
40 | Restoration of red stone road / footpath / pavement/ Paverblock upto 4 cm thickness | Item40 | 900 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
41 | BORROWED SELECT SOIL FOR BACKFILLING Additional work over and above item 1.0 for supply of specified and approved quality of borrowed soft graded soil / sand in place of available excavated material and / or other suitable soil as per applicable standards / specifications, including backfilling of excavated trench for specified length after laying and padding of pipeline, including transportation of such special backfill material over all distances, complete. | Item41 | 900 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
42 | CROSSING OF STEEL PIPELINE BY OPEN CUT | Item42
43 | Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insatllation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed. | Item43
44 | Road Crossing By Open Cut Method Road Crossings at various locations by Open cut Method as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item44 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
45 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method | Item45 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
46 | Water body Crossing By Open Cut Method water/ canal/ nallah/ drain/ channel Crossings at various locations by Open cut Method as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item46 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
47 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method | Item47 | 90 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
48 | Note: Laying of the pipeline by the approved method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item48
49 | Backfilling of the Road/water/ canal/ nallah/ drain/ channel Crossings/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority. | Item49
50 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item50 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
51 | CROSSINGS/LAYING ALONG THE ROAD BY HDD METHOD | Item51
52 | Complete work of the any crossing (between the limits are defined as approved drawings) by HDD method including "Receiving and taking over" owner supplied three layer PE coated line pipes from Owner's designated place to issue/ dump site(s) and transportation to Contractor's stock yard/ work shop/ work site including all handling loading, unloading, aligning etc. supply of all Contractor supplied material, manpower, equipment, other resources and aquiring the required land for storage, fabrication inclduing string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type Heat Shrink Sleeve and repair of pipeline coating with special repair patch materials as per specification,pre-testing etc. of complete string made for crossing access for Contractor etc and execution of, but not limited to, following works in accordance with specifications scope of work and instructions of Engineer-in-charge and as per all provision of Contract Document. | Item52
53 | Pre-construction surveys based on site visit, collection of historical data from irrigation/ concerned department including design & calculation and detail engineering and making of crossing drawing for getting their approval from concerned Authority/ Engineer-in-charge, getting work permit/ NOC for water crossings/ road crossings as well as utility crossings (if any) encountered during crossing prior to start the execution of work. | Item53 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
54 | Directional drilling to required depth from top of road including maintenance of drill hole in all types of strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) at all depth to accommodate the pipeline at all conditions encountered during rail/ road crossing by approved HDD methods for providing minimum cover specified in code/ specification or the actual depth as decided by concerned authority, whichever is more. | Item54 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
55 | In case of water crossing, drilling to the required depth on the banks and bed including maintenance of drill hole in all types of soil strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) all depth to accommodate the pipeline a by HDD methods for providing with minimum cover over top of the pipe at all point across the maximum possible width of water bed (as per drawing) either 1.5 mtrs. below the predicted scour profile expected during the life time of the pipeline or 2.5 mtrs. below the available lowest firm bed (if scour profile/ depth not available) of the water crossing by ascertaining bed level upto 50 mtrs. both the side from crossing location or the actual depth as decided by concerned Authority/ Engineer-in-charge whichever is more. | Item55 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
56 | Laying of the pipeline by the approved HDD method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints with special type Dirax Heat Shrink Sleeve or equivalent and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item56 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
57 | Backfilling of the ditch/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority and all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specification, approved drawings, calculations, methods and to the satisfaction of Engineer-in-charge and/or as directed by concerned Authority. | Item57 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
58 | Post installation hydrotest dewatering and tie-in with pipeline at either side of crossing/banks etc. | Item58 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
59 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item59 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
60 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 by HDD Method . | Item60 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
61 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item61 | 120 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
62 | Installation of carrier pipes by rock drilling for Road/water/Canal/ nallah/ drain/ channel/along the road, or wherever required in all types of hard rock. It includes survey of the underground utilities, submission of profile for approval, execution of the work as per the standard procedure, including , excavation of the pits, insertion/pulling of the carrier pipe, removal of malba, subsequent backfilling and restoration of the facility crossed as per original condition, including supply of all other materials, equipment, consumables, manpower etc including string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type of Heat Shrink Sleeve (Direx) and repair of pipeline coating with special repair patch materials as per Specification, pre-testing etc. of complete string made for crossing/ laying access for Contractor etc. and execution of, but not limited to, following works in accordance with specifications and instruction of Engineer-in-Charge and as per all provision of Contract Document. Balance activities as defined in SOR Item of open trench. Note:The length of HDD mentioned is tentative and may vary to the considerable extent depending upon requirements as per site conditions. The length mentioned in SOR is indicative for all the crossing to be done by HDD, numbers and locations shall be decided by Engineer-in-Charge depending upon site condition. Payment for the length of final tie-in carrier pipeline string with mainline laid by HDD are inclusive in this above item rate. No separate payment shall be made under other clauses mentioned elsewhere. Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item62
63 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 by HDD Method . | Item63 | 120 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
64 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item64 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
65 | Note: (i) Crossing width & Actual string length for HDD shall vary as per design calculations & site condition so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. | Item65
66 | (ii)Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item66
67 | (iii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by HDD method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item67
68 | (iv) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossing at different locations. | Item68
69 | (v) The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. | Item69
70 | Note: (i) Quantity mentioned under item nos. 44, 46 are indicative only for different location of roads/water/ canal/ nallah/ drain/ channel Crossings. (ii) Actual length & width of individual crossing and cover from top of casing pipe/ carrier pipe string may vary depending upon site condition, approved crossing drawings, specifications etc. and / or as decided by Engineer-in-charge/ Concerned Authority. | Item70
71 | (iii) Payment for supply & installation of Zinc ribbon anode and its design excluded from above item and covered elsewhere in the SOR. (iv) Payment for the length carrier pipeline string inserted in casing pipe laid by Boring are covered separately and shall be paid under other clauses mentioned elesewhere in the SOR. | Item71
72 | Excavation beyond 1.5m depth in case of crossing of utilities/ drain/ culverts etc. through open cut upto the following depth (including restoration of the damaged area to its original condition and satisfaction of the Engineer-in-charge / concerned authorities) : - | Item72 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
73 | In all type of surface (Kachha/ built-up surface / Hard surface) of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. The other activities are as per SOR 1.1. Payment for cutting of hard rock, if any, is covered unders SOR no. 76 | Item73
74 | Deeper than 1.5 m & upto 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item74 | 800 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
75 | Deeper than 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item75 | 300 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
76 | Excavation of hard rock | Item76
77 | Excavation of hard rock wherever hard rock of single piece exceeding 1.0 m in length removable by pneumatic chisel/ drill as per direction of EIC. | Item77 | 3800 | Cub. M |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
78 | REPAIR OF COATING DEFECTS (NOT ATTRIBUTED TO CONTRACTOR) | Item78
79 | Repair of Holiday in Coating (Noted and recorded at the time of "receiving and taking over") Supply of all coating repair materials as per requirements of specification to be compatible with line pipe coating material, supply of all consumables, utilities, equipments and all manpower required, pipe cleaning and surface preparation, repairing of coating defects (resulting in holiday) and testing including all handling, transportation, etc. for line pipes, performing all works necessary for the completion of the works stirctly in accordance with relevant specification and instructions of Engineer-In-Charge. This rate shall be applicable per sq. cm of the exposed steel area exposed steel area. | Item79 | 2200 | Sq. cm. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
80 | PERMANENT MARKERS Supply, fabrication and installation of all types of permanent markers along the route including all associated civil works such as excavation in all types of soil, construction in all types of soil, construction of pedestals and grouting with concrete, clearing, supply and application of approved colour and quality of primer and paint, stencil letter cutting for numbers, direction, change etc., restoration of area to original condition and performing all works as per drawing, specification and instruction of engineer-in-charge. | Item80
81 | Pipeline RCC boundary / route marker as per drawing | Item81 | 120 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
82 | Pipeline warning markers with post & foundations | Item82 | 40 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
83 | Pipeline direction marker with post & foundations | Item83 | 25 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
84 | Pipeline KM with post & foundations | Item84 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
85 | HOOK -UP | Item85
86 | Hook-up of proposed pipeline by welding of final tie-in-joint with any existing laid pipeline portion of river X-ing ,existing Tap-off & battery limit of section IV including Hook-up point of the existing pipeline to be made ready for welding by cutting of flanges / valves / headers at all depth in all type of soil etc. Venting of N2 / gas / gas mixture as required purging of N2 Gas (if required), rebevelling as required, radiography and other NDT examination, joint coating as per specification.Contractor shall supply of all consumables, manpower, machinaries, materials, N2 gas etc. and carry out all works as per the provisions of Contract document and instructions of Engineer-in-charge. | Item86
87 | For 12" NB | Item87 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
88 | PRE-COMMISSIONING AND ASSISTANCE IN COMMISSIONING OF PIPELINE SYSTEM Swabbing, drying, purging with nitrogen of the complete pipeline network and the associated facilities being installed to the specified acceptance criteria, carrying out pre-commissioning works, providing assistance during the complete duration of commissioning operations for entire pipeline network system including supply of all equipment, man-power, consumables (including pigs & nitrogen required for purging with maintaining nitrogen column of mininum 10% of pipeline geometric volume) materials for all temporary works and performing all associated works, complete as per the relevant specifications, other provisions of Contract document and instructions of Engineer-in-charge. | Item88
89 | For 12" NB Pipeline | Item89 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
90 | IDLE TIME PRESERVATION OF PIPELINE Preservation of complete pipeline and associated facilities forming part of the pipeline as per Bid document and its maintenance including supply of all consumables, all equipment, manpower, etc. complete as per the requirements of specifications, other provisions of Contract document and instructions of Engineer-in-charge. Note : Owner reserves the right to exercise either or none of the rates below. | Item90
91 | By filling and pressurizing with nitrogen to a pressure of 2 bar(g) for a period of 3 months. | Item91 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
92 | For 12" NB Pipeline | Item92 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
93 | For every additional period of one month or part thereof | Item93 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
94 | For 12" NB Pipeline | Item94 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
95 | RCC VALVE PITS All civil works including supply of all materials, excavation of pit, piping supports including all PCC and RCC works for valves pits including pedestals with insert plates as required sealing of pipe at valve pits, providing cover etc. and finishing , clean-up and restoration of site, filling and grading of area around valve station for avoiding any local flooding of area, as per typical drawing and specification enclosed and instructions of Engineer-in-charge. In this item, instead of Brick Work, RCC will be done | Item95 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
96 | Valve Pit of Size 2m x 2m | Item96 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
97 | SUPPLY OF ASSORTED PIPE, FITTINGS AND FLANGES Complete works of supply of pipes, flanges & fittings for aboveground & underground installation including all taxes, duties, transportation and inspection charges but not limited to, the following items in accordance with PMS (piping material specification), relevant specifications & drawings indicated in job specification under SCC (technical) and instructions of Engineer-in-charge and as per all provisions of the CONTRACT DOCUMENT. - Handling including lifting, transportation from Contractor Stores to CONTRACTOR's workshop for fabrication and/ or to work site for field fabrication and erection for all piping items supplied by Contractor. | Item97
98 | Carbon Steel Pipe (A 106, Seamless B-36.10/ API X 52 ) | Item98
99 | Size Rating/ Schedule | Item99 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
100 | 2" NB, BE Sch. 80 | Item100 | 55 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
101 | 1" NB, PE Sch. 80 | Item101 | 36 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
102 | ¾" NB, PE Sch. 160 | Item102 | 32 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
103 | Flanges | Item103
104 | Weld Neck (B-16.5, 300# A105,125 AARH, Serrated finish) | Item104
105 | Size Rating/ Schedule | Item105 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
106 | 2" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item106 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
107 | Blind Flanges (B-16.5, 300# A105,125 AARH Serrated) | Item107
108 | Size | Item108
109 | 2" NB, RF | Item109 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
110 | Elbow (Seamless) | Item110 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
111 | 90° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item111
112 | Size Rating/ Schedule | Item112
113 | 12" NB 300# | Item113 | 25 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
114 | 45° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item114 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
115 | Size Rating/ Schedule | Item115
116 | 12" NB 300# | Item116 | 22 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
117 | 90° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item117 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
118 | Size Rating/ Schedule | Item118
119 | 12" NB 300# | Item119 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
120 | 45° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item120
121 | Size Rating/ Schedule | Item121
122 | 12" NB 300# | Item122 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
123 | 22½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D) Min Thickness 6.4mm | Item123 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
124 | Size Rating/ Schedule | Item124
125 | 12" NB Sch. Std. | Item125 | 14 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
126 | 11½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D), Min Thickness 6.4mm | Item126
127 | Size Rating/ Schedule | Item127
128 | 12" NB 300# | Item128 | 14 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
129 | Tees (Seamless) | Item129
130 | Equal Tee (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item130
131 | Size Rating/ Schedule | Item131
132 | 12" NB x 12" NB x 12" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item132 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
133 | 2" NB x 2" NB x 2" NB Sch. XS | Item133 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
134 | Weldolet and Sockolet | Item134
135 | Weldolet (MOC A105 & DIM. MSS SP 97) | Item135
136 | Size Rating/ Schedule | Item136
137 | 12" NB x 2" NB Sch. 80. | Item137 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
138 | Sockolet (MOC A105 & DIM. MSS SP 97) | Item138
139 | 12" NB x 3/4" NB #6000 | Item139 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
140 | Butt Weld Disc End Cap (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item140
141 | Size Rating/ Schedule | Item141
142 | 12" Sch. Std. | Item142 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
143 | Fabrication & Installation of Underground Valve Assembly | Item143 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
144 | 12"NB Isolation Valve/tap-off assembly as per Drg. No. MNGL/Plng./Steel/40 | Item144 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
145 | Note: | Item145 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
146 | For all the supply items mentioned above, procurement shall be made as per enclosed Data Sheets and respective technical specification, after due approval of Engineer-in-charge. | Item146
147 | The quantities mentioned above are tentative and quantities for above supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item147
148 | PLANT PIPING (ABOVEGROUND) Fabrication and testing of carbon steel piping and fittings, valves, IJ, including supply of all consumables, equipment, manpower, and other resources and execution of job as per instruction AIC/EIC.Transportation of all piping items from Owner's and/ or Contractor's storage point to work at site/ workshop as applicable, complete work of fabrication, erection, painting, testing of pipes, flanges and fittings and making ready for further Commissioning / Start-up of carbon steel piping of all sizes and ratings including supply of all consumables, equipment, manpower and other resources and execution of, but not limited to, as per all provisions of the CONTRACT DOCUMENT. | Item148 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
149 | Fabrication including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site, cutting, edge preparation, inclusive of grinding the edges of pipes, fittings, flanges, reducers etc. to match with the matching edges of uneven thickness, wherever required, fit-up, welding of pipes and fittings like elbows, tees, reducers, weldolets, sockolets, Valves, IJ etc. flanges, vent and drain point connection, Radiography and NDT of all joints etc, including providing stubin connections, fabricated fittings and reinforcement pads etc., as required. | Item149 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
150 | Erection of pipes of all types and thickness at all elevations, connecting with equipment nozzle, aligning, installation and carrying out connected activities for all types of valves, all online instruments and fittings of all sizes of elbow, reducers, tees, flanges, blind flanges, spectacle blind flanges, branch connection / tapping for pressure gauges, including installation of gaskets and bolts. | Item150 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
151 | Erection including prior cleaning, lifting, placing on pipe sleepers and supports, overhead on racks, skids and at all elevations including installation and carrying out connected activities for all types of valves including supply and fixing of gaskets, studs/ bolts, nuts wherever required for all sizes, levelling, aligning, joining of flanges, blind flanges, connecting with equipment, nozzles, strainers, tie-in with existing piping/facilities, etc. tapping for inline instruments like pressure gauges, thermowells, sample connection, etc. | Item151
152 | Hydro testing of the piping job shall be conducted at pressure mentioned in specification for a period of 4 hours by using de-mineralised water, to check its strength. No visible leakages shall be detected during the test. Testing shall be conducted as per tender specification. | Item152
153 | Preparation of final bill of material based on piping GADs. | Item153
154 | Preparation of isometric and fabrication drawings. | Item154
155 | Carrying out Non-destructive testing as required | Item155
156 | Painting of entire system (including aboveground all pipes fittings, flanges and accessories) as per specifications suitable for highly corrosive area environment including supply of approved paints and primers, application of primer and paints, indentification lettering/ numbering, colour coding, etc. as specified including rub down & touch up of shop primer or scrapping of shop primer wherever required by COMPANY and providing scaffolding for all heights etc. | Item156
157 | Cleaning and flushing by water/ compressed air, testing of the systems including hydrostatic, pneumatic and any other type of testing as specified, draining, drying by compressed air/other methods approved by COMPANY. | Item157
158 | Precommissioning & making operational all piping system and equipments. | Item158 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
159 | Commissioning Contractor scope shall provide all necessary assistance in term of supply of man-power, equipment, tools and tackles required amount of nitrogen for purging of entire terminal piping system including equipments etc. to the company during commissioning activities. | Item159 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
160 | Completion of all such work in all respects as per scope of work and as per drawings, specifications and instructions of the COMPANY and keeping the system ready in all respects for further commissioning and start up. | Item160 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
161 | Hook-up works (with client/ consumer piping at battery limits): | Item161 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
162 | Complete Carbon Steel aboveground Piping Work with painting including all fittings, flanges and supply of all required gaskets, studs bolts & nuts etc. and Any other work and material required for the completion of the work and not covered above and desired by EIC shall be in the scope of contractor | Item162 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
163 | Carbon Steel Pipe (ASTM A 106, Seamless B-36.10 / API X 52) | Item163 | 150 | inch Dia |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
164 | 1) Pipe Specification and thickness may vary depending upon availability of pipe. No extra payment shall be made for this. 2) All butt welded fittings & flanges end shall generally match with connecting pipe wall thickness. However, in case of misalignment, Contractor shall have to do end preparation without any extra cost. 3) All o-lets less than 2" NB size, all sizes of coupling and nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under erection rate. | Item164 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
165 | Aboveground installation of Insulating Joint & Valves etc. Handling including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site and installation of all types of valves, insulating joint including assembly of valve accessories, (if any) by bolting, threading or welding, supply and insertion of gaskets, nuts & bolts, nipples, etc. at all elevations of pipe sleepers, supports or overhead on racks, equipments nozzle, skid & painting etc. supply of all consumables, manpower, equipment, etc. for completion of all works as per scope of work and as per drawings, specifications and instructions of Engineer-in-charge including servicing/ cleaning of valve wherever requried. | Item165 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
166 | 12" NB, 300# - Insulating Joints | Item166 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
167 | STRUCTURAL WORKS | Item167 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
168 | Supply of erection of single leaf mild steel gate 2.5m high with mesh upto 2m height and barbed wire fencing and 2m wide complete in all respect including painting as per TS on all MS items, all works as per specification and drawings excluding foundations and RCC beams. | Item168 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
169 | Supply of all materials, fabrication and erection of chain link fencing 2.5m high with mesh up to 2m height and barbed wire fenching complete in all respects including painting as per TS on all MS items, all works as per specification and drawings excluding foundation and RCC beams. | Item169 | 200 | RM |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
170 | Pipe Supports & Other Structures | Item170 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
171 | Supply, fabrication and erection of all types of pipe supports like clamps, saddle, guide stops, cradles, turn buckles, anchors, T-posts; stockade/ trestle and pipe bridge for overhead piping; frames for canopy, approach ladders and platforms, crossover, cable tray supports, etc. including painting suitable for highly corrosive area as per specification labour and supervision & complete work as per drawings, specifications and instruction of Engineerqw-incharge. (Bolts, nuts, washers, U-clamps etc. for supporting shall be supplied by the Contractor within the rates quoted. These items will not be measured and paid seperately). The work is to be completed in all respect as per scope of work and specification. | Item171 | 250 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
172 | Notes: | Item172 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
173 | The quantities indicated are estimated values and hence are approximate. Final payment will be made based on actual quantities to be certified by the Purchaser. | Item173
174 | The cost of MS bolts (permanent and service(, washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants etc., as required for the work shall be deemed to be included in the quoted rates. | Item174 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
175 | All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accrodance with time schedule, are deemed be included in the quoted rates. | Item175
176 | CIVIL WORKS | Item176
177 | Site Grading Excavation in earth and filling to the grades and levels shown in the approved drawings in all kinds of conditions including for Road embarkments, using approved quality good earth from designated borrow area, for all heights and depths including clearing and stripping (min. 150mm) of the area marked for filling, taking spot levels, consolidating the exposed natural soil surface, excavating the earth from borrow area loading, transporting & unloading, spreading in layers not exceeding 150mm thickness, breaking clods, watering (if reqd.), ramming and compacting by manual/ mechanical means to give minimum 92% of modified Proctor's density of earth, testing & dressing including disposal of all unserviceable material all complete as per specifications and directions of Engineer-in-charge. | Item177 | 300 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
178 | (Rate to include cost of all labour, tools, tackles, equipment, hire charges, cost of borrow earth by way of royalties, right of way, cess etc., as applicable with all bye works and sundry works). | Item178
179 | Plain Cement Concrete Supplying and laying plain cement concrete (including shuttering of required) in all types of concrete works including levelling courses below foundation, substructure, superstrcuture, chambers, cable tranch, under floors and any other locations, at all leveies as per drawings, specifications and directions of the Engineer-in-charge. | Item179
180 | PCC 1:2:4 1 Cement : 2 Coarse sand : 4 stone aggregate 20mm nominal size. | Item180 | 500 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
181 | Reinforced Cement Concrete Providing and laying reinforced cement of grade M-20 with 20mm and down grade crushed stone aggregate in all types of structures like foundations, pedestals, pedestal bases, pipe supports, sleepers cable trench inlcuding constrcution joints, bitumen painting on surface in contact with soil, providing and fixing reinforcing steel, shuttering, inserts, finishes etc. at all depths and heights complete as per drawings, specifications and direction of the Engineer-incharge. | Item181 | 400 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
182 | Rate to include cost of all labour, tools, tackles, equipment, hire charges, supply of all maerials such as minimum 43 grade cement including sulphate resistant cement for substructures, R/F steel, Inserts, bolts, conduits, bitumen, other minor constrcution materials, shuttering, stanging, earthwork in excavation and backfilling using serviceable earth in all conditions, shorting bailing and pumping out water, testing of concrete, curing etc. with all bye works and syndry works. | Item182
183 | TEMPORARY CATHODIC PROTECTION SYSTEM | Item183
184 | Design, detailed engineering, supply, installation, testing and commissioning of the temporary Cathodic protection system using Mg/ Zn galvanic anodes to protect the external surface of 3 LPE coated entire 5.5 km (approx.) long steel pipeline network against corrosion for design life of minimum 1 year or till commissioning of PCP system whichever is later as per standard specification No. MNGL/Steel/TS/15 for temporary cathodic protection system. Scope shall also include but not limited to the following for completion of jobs: | Item184 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
185 | Measurement of soil resistivity along the right of way of the main pipeline route as per specification for design & installation of anodes. | Item185
186 | Collection of additional data related to cathodic protection along the right of way of pipeline as per specifications. | Item186 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
187 | Supply, installation, testing & commissioning of one set of spark gap arrestor with 2 plate Zinc grounding cell of 20 kg net weight each across each insulating joint as per specification. | Item187
188 | Supply, installation, testing & commissioning one set of polarisation cell with zinc anode at all high tension (66KV or higher) electrical power transmission line/Equipment crossing or running parallel to the pipeline for grounding purpose as per specification. The rating shall depend upon anticipated fault current & ground bed resistance at the location of installation. However, the rating of polarisation cell (krick) shall not be less than 5 KA & number of 20 kg net weight zinc anode shall not be less than two. | Item188
189 | Supply & installation of Zinc Ribbon Anodes at 4-8 O’Clock position in the interval of 2 metre (max.) on carrier pipes at all cased crossings i.e. railways/ roads etc. | Item189 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
190 | Monitoring of the protection system for 6 months. | Item190
191 | All civil/ structural works related to TCP system including supply of bricks, cement & steel etc. required for completion of the system. | Item191 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
192 | For 12" | Item192 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
193 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item193 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
194 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item194 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
195 | FIELD INSTRUMENTATION | Item195 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
196 | PRESSURE INSTRUMENTS | Item196
197 | Supply , Installation of Pressure Gagues and their accessories inclusive of supply of necessary piping materials and tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/ manifolds & hydraulic testing (exclusive of calibration of instruments) as per installation standard attached elsewhere in Tender Document and Supply as per Data Sheet No.MEC/23K8/05/E5/I/001/DS-PG. Give breakup of supply and Installation rate. | Item197 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
198 | CALIBRATION | Item198
199 | Calibration of the instruments listed below including removal of instruments from pre-installed locations like panels, enclosure racks, fields etc. and refixing them back in respective/ required places, providing equipments, necessary test jigs, instrument air and all consumables. Calibration reports shall be prepared and to be submitted to the Purchaser/ Consultant. | Item199
200 | Pressure Gauges | Item200 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
201 | Note: | Item201 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
202 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item202 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
203 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item203 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
204 | PIPING WORKS FOR SECTIONALISING VALVE STATION-CUM-TAP-OFF POINT All works for fabriaction and installation of all piping above ground at all elevations and below ground at all depth for Sectionalising Valve Station alongwith preparation of construction drawings duly approved by EIC, in all type of terrains and soils including transportation and handling of all Owner supplied materials i.e. extended stem butt welded sectionalising gas actuated ball valve, other types of valves, line pipes for mainline, 4" NB pipe for all branch line including ventlines from Owner's designated place(s) of issue to work site. | Item204 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
205 | Contractor shall supply all required size & type of piping material like pipes, fittings & flanges etc. as per PMS alongwith 2" NB pipe for all branch line & vent line (wherever required) including supply of all consumables, manpower, machinaries, materials etc. and carrying out all mechanical works of underground and above ground piping including fabrication, welding, nondestructive testing of welds, weld repairs/ retesting, cleaning/ flushing, pre-hydrotesting & hydrostatic testing, dewatering, functional testing, cutting of mainline and bevelling (if required) | Item205
206 | assembly, including radiography of tie-in joints, corrosion, coating and external painting as required, installation of instruments like pressure/ temperature instruments/ gauges alongwith complete SS Tubing works including supply of SS Tube and thier accessories etc., as required, obtaining all statutory clearances, approvals and permissions for the works (wherever required), making of valve pit (for detail refer relevant drawings) for SV Stationscum- tap-off points enclosed with tender filled with sand, excavation and filling in all types of soils including soft/ hard rock for installation of piping/ pipe supports providing pipe supports, area fencing and gate including all associated civil and structural works; painting, finishing, clean-up and restoration of site; preparation of as-built drawings, documents and project records and performing all works as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge. In this item, instead of Brick Work RCC will be done | Item206 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
207 | Type - I SV Station on 12" Pipeline | Item207 | 1 | Lumpsum for each |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
208 | Note: i) Work under above items are exclusive of all works associated with main pipeline covered under Item No. 1.0 above. ii) All civil/ structural works including area fencing and gate, valve pits except for piping support will be paid separately as per unit rate provided elsewhere in the SOR. iii) All coupling, nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under above item rate. | Item208 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
Total in Figures | [51 empty] | 0 | 0 | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## BoQ10 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR | [49 empty] | 1
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Maharastra Natural Gas Ltd.,Pune
Name of Work: TENDER FOR LAYING & CONSTRUCTION OF 12” NB X 6 KM U/G STEEL PIPELINE NETWORK & ASSOCIATED WORKS FROM NEAR CHIKHALI VILLAGE ROAD, CHIKHALI TO NEAR HOTEL SAMRUDDHI, TALEGAON ON NH 548C (Section No-10)
Tender No: MNGL/CP/2024-25/109
Do you want to quote for this sheet ? |  |  | Yes
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE / SCHEDULE OF RATES (SOR) (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Rate inclusive of all taxes and duties except Goods & Service Tax (Rs.) | Per Unit Goods & Service Tax (GST) In % (To be entered by the Bidder) | GST in Rs. | Unit rate inclusive of all taxes & duties including GST (Rs.) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | CARBON STEEL PIPES | Item1
2 | PIPELINE LAYING / INSTALLATION in all type of surface (Normal/built-up surface) "Receiving and taking over" as defined in the specifications, handing, loading, transportation and unloading of Owner supplied 3-Layer PE coated linepipes from Owner's designated stack-yard to Contractor's stock yard/workshop/work-site including preliminary activities, preparation of drawings, wherever required for crossing etc. including handling, stacking, stringing on the pipeline Right-of-Use/ pipeline route alignment, carrying out inspection of company supplied materials including linepipes at the time of taking over, laying/ installation of coated linepipes, associated burried valves, barred tees, insulating joints, flanges & fittings of all sizes, thickness & ANSI class rating and accessories as per specification wherever required depending on site condition including execution of all works, "taking over", handling , including loading and unloading, transportation of Owner supplied materials other than linepipe from Owner's designated place (s) of issue to work site, | Item2 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3 | additional lands required for Contractor's storage, fabrication, access for construction, procurement and supply of all materials (except Owner supplied materials), consumables, equipment, labour and other inputs, carrying out all temporary, ancillary, auxiliary works, aquistion of ROU/ROW for laying of pipeline from HDD Exit and entry point to Tie in Point of existing Pipeline/ ROU, ready for commissioning of pipeline as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge, including but not limited to carrying out the following works: | Item3 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4 | Surveying of route and detours required at the time of execution including marking the same in topographical sheet, preparation of construction drawings showing survey details, and submit same to Owner for review / approval. | Item4
5 | Staking and installation of construction markers, clearing, fencing, grubbing, cutting of trees, full filling all the requirements of various statutory/ environment authorities to the entire satisfaction of concerned authorities, grading of work area. Shifting of all obstruction within the ROU/ Pipeline route alignment viz. electrical lines/ poles, telephone line / poles, etc. coordination with concerned authorities and obtain permissions from these authorities. | Item5
6 | Trenching to all depths by excavation in all types of soils including soft/ hard rock and different type of pavement / footpath / roads etc. including rock breaking, chiselling or otherwise cutting etc. as required and storing excavated soil, reusable materials at designated area as directed by Engineer in charge and to a width to accommodate the Steel pipeline as per the relevant standard/ specification etc. [The minimum depth of the top of pipeline shall be 1.2m measured from top of pipeline coating to the top of undisturbed surface of the soil or as per SCC/ OISD - 141 / 226, whichever is higher]. Dewater of trenches if required as per site condition. | Item6
7 | Carrying out repairs of pipe defects/ replacement in case of irreparable defects and repairs of defects of pipe coating not attributable to Owner including defects/ damages occurring during transportation / handling. | Item7
8 | Stringing of line pipes along pipeline trench / ROU on straw / sand / soft soil bags including supply of bags and its filling materials. | Item8
9 | Checking, cleaning, aligning, bending, cutting and bevelling (as required) of pipes for welding and field adjustments including pipe fittings, welding, carrying out non-destructive testing of welds as required including 100% radiography by X-ray and providing all requisite equipment, labour, supervision, materials, films, consumables, all facilities and personnel to process, develop, examine and interpret radiographs and other tests as required, carrying out repairs of weld joints found defective by Engineer-in-Charge, carrying out re-radiography and other tests as required on repaired joints. | Item9
10 | Carrying out installation of carrier line pipe at all minor crossing viz. carttrack, pathway, water bodies etc. at designated depth by open cut (except at crossing by HDD method). | Item10
11 | Carrying out installation of carrier line pipe in the casing pipe at cased crossing (excluding installation of casing pipes which is covered separately). | Item11
12 | Coating of field weld joints, long radius bends (R=3D), elbows, buried fittings and valves etc. including supply of coating materials etc. (i.e. heat shrinkable sleeves and high build epoxy etc.) as per PJS & Technical Specification compatible with 3 layer PE coating material of the line pipe. | Item12 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
13 | Counting the number and type of trees cut in presence of DFO/concerned authorities and keeping record thereof, stacking and handing over of all cut tress. | Item13
14 | Installation / lowering the pipeline in trench to required depth as per PJS, Techanical Specification & drawings, supply & placement of 1.0mm thk. HDPE Yellow colour warning mat,RCC tiles (300 mm width x 50 mm thick) over the pipeline in same trench along the complete route as per standard drawings, data sheets & technical specifications, padding around pipeline as per Standard Drg. no. MNGL/Plng./Steel/03 with suitable soil duly approved by EIC including supply of padding material, backfilling and its compaction to the satisfaction of concerned authorities with excavated earth / borrowed select soil including supply of borrowed select soil duly approved by EIC before backfilling and make ready for restoration to be done by Onwer / concerned authorities. | Item14
15 | Supply and installation of slope breakers, wherever required or, as directed by Onwer / Engineer–in–charge. | Item15
16 | Crossing the all-foreign pipeline / HT line / cable / any other utilities etc. with necessary concrete / HDPE sheet protection including coordination with all agencies and obtaining NOC | Item16
17 | Supply and installation of bank protection alongwith backfill materials duly approved by EIC for pipeline trench and banks falls under minor water body crossing as per technical specification & Std. Drg. No. MNGL/Plng./Steel/28, wherever required or, as directed by Onwer / EIC. | Item17
18 | Training and diversions of streams in steep slope area, wherever required. | Item18
19 | Carrying out air cleaning, pigging, flushing, cleaning and hydrostatic testing of complete pipeline with required quantity of corrosion inhibitor including pre-testing of designated sections complete as per specification and approved by Engineer–in–charge to specified pressures indicated elsewhere and duration after stabilization as per specification, providing all equipment, pumps, fittings, instruments, dead weight tester, pressure recorder, thermocouples etc., and services, supervision, labour, consumables, water including supply of corrosion inhibitor, air, etc. as required, locating of leaks and rectification of defect attributable to Contractor (rectification of defects in linepipe material not attributable to contractor shall be paid separately as per other item of schedule of rate), re-testing after rectification, dewatering after successful completion of hydrotesting of entire section and as per specification | Item19
20 | All tieing-in, including the tie-in(s) of the pipeline with the adjacent sections of pipeline including cutting of test header, rebevelling as required, radiography and other NDT examination, joint coating as per specification. | Item20
21 | Final clean-up of right-of-use or area disturbed by contractor during their construction activities for laying of pipeline works and disposal of debris and surplus material to designated disposal areas and backfilling of trench and compaction of the same as per satisfaction of Owner and / Or as directed by Engineer–in–charge. | Item21
22 | Installation of all burried valves (except extended stem valves) inside the valve pit and making provision to operate the valve. | Item22 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
23 | Preparation of as-built drawings, pipe-books (1 set of tracing on polyester film and 6 sets of as-built drawings and 1 soft copy and 6 hard copies of pipe book) All the works shall be executed in accordance with the provision of contract including carrying out all temporary/ ancillary/ auxiliary works required for the performance of the works and all other acts, deeds, matters and things necessary to make the pipeline ready for precommissioning activities. | Item23 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
24 | Raking up of hard surface of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. Payment for cutting of hard rock, if any, is covered unders SOR no. 76 | Item24 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
25 | Specified dia Thk (mm) Material Coating Type Length of each pipe (mm) NB | Item25 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
26 | 305 (approx.) 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item26 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
27 | Note: This item shall be applicable for the underground steel grid main pipeline & branch pipeline, barred tees, insulating joints, bends, flanges & fittings, accessories etc. (i.e. including arrangement for making provision for tap-off on proposed steel grid main pipeline) and aboveground approach pipeline upto Insulating Joint (excluding installation of aboveground insulating joint) for various stations. | Item27
28 | Items except above are covered separately. The lengths of pipelines are tentative. | Item28 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
29 | Permission Liasioning /Follow-up | Item29 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
30 | Liasioning & follow up for Permission with all the concerned authorities & boards viz Railways, NH, PWD, MIDC, Local Municipal, Panchyat, Electricity, REC, RES, Sewage water, Drinking water, Forest, Social Forestry, Owners of OFC, Traffic, Law & Order, Fire Brigade, Private Land Owner etc. for entire pipeline length and associated terminals (like SVs, tap-offs) alongwith associated work as per tender. | Item30 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
31 | Laying of RCC Tiles | Item31 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
32 | Providing single layer of RCC Tiles with supply of RCC Tiles to entire width of trench above Warning Mat placed in trench over the laid pipeline as per standard drawing, specification and instruction of Owner. (Rate to include cost of all labour, tools, tackles, equipment, hire charges & supply of all materials, etc.) | Item32
33 | For width of 12" pipeline trench | Item33 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
34 | Barricading to comply with HSSE | Item34 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
35 | Steel barricading of the trenches Cautionary Sign Boards and lighting arrangement shall be provided as per attched drawing no.MNGL/Plng./steel/04. The rates include barricading of trenches along with sign boards, lighting etc. and maintain the same till the back filling of the trench. Rates will be payable per metre of BARRICADING PROVIDED. If proper barricading is not provided, MNGL will barricade the trenches at the risks and costs of the CONTRACTOR and will levy penalty of twice the rate per unit for the relevant section of the pipeline apart from other actions as per contract. | Item35 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
36 | RESTORATION OF ROADS Restoration of asphalt / concrete / red stone roads / pavement/Footpath/Paver block including compaction of soil, to original condition as per requirement and to the entire satisfaction of EIC and / or concerned Owners having jurisdiction for following thickness. | Item36 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
37 | Restoration of Asphalt road upto 10 cm thickness | Item37 | 800 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
38 | Restoration of Asphalt road beyond 10 cm upto 20 cm thickness | Item38 | 200 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
39 | Restoration of Concrete road upto 10 cm thickness | Item39 | 800 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
40 | Restoration of red stone road / footpath / pavement/ Paverblock upto 4 cm thickness | Item40 | 900 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
41 | BORROWED SELECT SOIL FOR BACKFILLING Additional work over and above item 1.0 for supply of specified and approved quality of borrowed soft graded soil / sand in place of available excavated material and / or other suitable soil as per applicable standards / specifications, including backfilling of excavated trench for specified length after laying and padding of pipeline, including transportation of such special backfill material over all distances, complete. | Item41 | 900 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
42 | CROSSING OF STEEL PIPELINE BY OPEN CUT | Item42
43 | Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insatllation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed. | Item43
44 | Road Crossing By Open Cut Method Road Crossings at various locations by Open cut Method as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item44 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
45 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method | Item45 | 90 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
46 | Water body Crossing By Open Cut Method water/ canal/ nallah/ drain/ channel Crossings at various locations by Open cut Method as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item46 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
47 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method | Item47 | 120 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
48 | Note: Laying of the pipeline by the approved method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item48
49 | Backfilling of the Road/water/ canal/ nallah/ drain/ channel Crossings/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority. | Item49
50 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item50 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
51 | CROSSINGS/LAYING ALONG THE ROAD BY HDD METHOD | Item51
52 | Complete work of the any crossing (between the limits are defined as approved drawings) by HDD method including "Receiving and taking over" owner supplied three layer PE coated line pipes from Owner's designated place to issue/ dump site(s) and transportation to Contractor's stock yard/ work shop/ work site including all handling loading, unloading, aligning etc. supply of all Contractor supplied material, manpower, equipment, other resources and aquiring the required land for storage, fabrication inclduing string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type Heat Shrink Sleeve and repair of pipeline coating with special repair patch materials as per specification,pre-testing etc. of complete string made for crossing access for Contractor etc and execution of, but not limited to, following works in accordance with specifications scope of work and instructions of Engineer-in-charge and as per all provision of Contract Document. | Item52
53 | Pre-construction surveys based on site visit, collection of historical data from irrigation/ concerned department including design & calculation and detail engineering and making of crossing drawing for getting their approval from concerned Authority/ Engineer-in-charge, getting work permit/ NOC for water crossings/ road crossings as well as utility crossings (if any) encountered during crossing prior to start the execution of work. | Item53 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
54 | Directional drilling to required depth from top of road including maintenance of drill hole in all types of strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) at all depth to accommodate the pipeline at all conditions encountered during rail/ road crossing by approved HDD methods for providing minimum cover specified in code/ specification or the actual depth as decided by concerned authority, whichever is more. | Item54 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
55 | In case of water crossing, drilling to the required depth on the banks and bed including maintenance of drill hole in all types of soil strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) all depth to accommodate the pipeline a by HDD methods for providing with minimum cover over top of the pipe at all point across the maximum possible width of water bed (as per drawing) either 1.5 mtrs. below the predicted scour profile expected during the life time of the pipeline or 2.5 mtrs. below the available lowest firm bed (if scour profile/ depth not available) of the water crossing by ascertaining bed level upto 50 mtrs. both the side from crossing location or the actual depth as decided by concerned Authority/ Engineer-in-charge whichever is more. | Item55 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
56 | Laying of the pipeline by the approved HDD method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints with special type Dirax Heat Shrink Sleeve or equivalent and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item56 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
57 | Backfilling of the ditch/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority and all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specification, approved drawings, calculations, methods and to the satisfaction of Engineer-in-charge and/or as directed by concerned Authority. | Item57 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
58 | Post installation hydrotest dewatering and tie-in with pipeline at either side of crossing/banks etc. | Item58 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
59 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item59 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
60 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 by HDD Method . | Item60 | 120 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
61 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item61 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
62 | Installation of carrier pipes by rock drilling for Road/water/Canal/ nallah/ drain/ channel/along the road, or wherever required in all types of hard rock. It includes survey of the underground utilities, submission of profile for approval, execution of the work as per the standard procedure, including , excavation of the pits, insertion/pulling of the carrier pipe, removal of malba, subsequent backfilling and restoration of the facility crossed as per original condition, including supply of all other materials, equipment, consumables, manpower etc including string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type of Heat Shrink Sleeve (Direx) and repair of pipeline coating with special repair patch materials as per Specification, pre-testing etc. of complete string made for crossing/ laying access for Contractor etc. and execution of, but not limited to, following works in accordance with specifications and instruction of Engineer-in-Charge and as per all provision of Contract Document. Balance activities as defined in SOR Item of open trench. Note:The length of HDD mentioned is tentative and may vary to the considerable extent depending upon requirements as per site conditions. The length mentioned in SOR is indicative for all the crossing to be done by HDD, numbers and locations shall be decided by Engineer-in-Charge depending upon site condition. Payment for the length of final tie-in carrier pipeline string with mainline laid by HDD are inclusive in this above item rate. No separate payment shall be made under other clauses mentioned elsewhere. Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item62
63 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 by HDD Method . | Item63 | 120 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
64 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item64 | 90 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
65 | Note: (i) Crossing width & Actual string length for HDD shall vary as per design calculations & site condition so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. | Item65
66 | (ii)Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item66
67 | (iii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by HDD method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item67
68 | (iv) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossing at different locations. | Item68
69 | (v) The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. | Item69
70 | Note: (i) Quantity mentioned under item nos. 44, 46 are indicative only for different location of roads/water/ canal/ nallah/ drain/ channel Crossings. (ii) Actual length & width of individual crossing and cover from top of casing pipe/ carrier pipe string may vary depending upon site condition, approved crossing drawings, specifications etc. and / or as decided by Engineer-in-charge/ Concerned Authority. | Item70
71 | (iii) Payment for supply & installation of Zinc ribbon anode and its design excluded from above item and covered elsewhere in the SOR. (iv) Payment for the length carrier pipeline string inserted in casing pipe laid by Boring are covered separately and shall be paid under other clauses mentioned elesewhere in the SOR. | Item71
72 | Excavation beyond 1.5m depth in case of crossing of utilities/ drain/ culverts etc. through open cut upto the following depth (including restoration of the damaged area to its original condition and satisfaction of the Engineer-in-charge / concerned authorities) : - | Item72 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
73 | In all type of surface (Kachha/ built-up surface / Hard surface) of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. The other activities are as per SOR 1.1. Payment for cutting of hard rock, if any, is covered unders SOR no. 76 | Item73
74 | Deeper than 1.5 m & upto 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item74 | 650 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
75 | Deeper than 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item75 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
76 | Excavation of hard rock | Item76
77 | Excavation of hard rock wherever hard rock of single piece exceeding 1.0 m in length removable by pneumatic chisel/ drill as per direction of EIC. | Item77 | 3800 | Cub. M |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
78 | REPAIR OF COATING DEFECTS (NOT ATTRIBUTED TO CONTRACTOR) | Item78
79 | Repair of Holiday in Coating (Noted and recorded at the time of "receiving and taking over") Supply of all coating repair materials as per requirements of specification to be compatible with line pipe coating material, supply of all consumables, utilities, equipments and all manpower required, pipe cleaning and surface preparation, repairing of coating defects (resulting in holiday) and testing including all handling, transportation, etc. for line pipes, performing all works necessary for the completion of the works stirctly in accordance with relevant specification and instructions of Engineer-In-Charge. This rate shall be applicable per sq. cm of the exposed steel area exposed steel area. | Item79 | 2200 | Sq. cm. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
80 | PERMANENT MARKERS Supply, fabrication and installation of all types of permanent markers along the route including all associated civil works such as excavation in all types of soil, construction in all types of soil, construction of pedestals and grouting with concrete, clearing, supply and application of approved colour and quality of primer and paint, stencil letter cutting for numbers, direction, change etc., restoration of area to original condition and performing all works as per drawing, specification and instruction of engineer-in-charge. | Item80
81 | Pipeline RCC boundary / route marker as per drawing | Item81 | 120 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
82 | Pipeline warning markers with post & foundations | Item82 | 40 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
83 | Pipeline direction marker with post & foundations | Item83 | 25 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
84 | Pipeline KM with post & foundations | Item84 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
85 | HOOK -UP | Item85
86 | Hook-up of proposed pipeline by welding of final tie-in-joint with any existing laid pipeline portion of river X-ing ,existing Tap-off & battery limit of section IV including Hook-up point of the existing pipeline to be made ready for welding by cutting of flanges / valves / headers at all depth in all type of soil etc. Venting of N2 / gas / gas mixture as required purging of N2 Gas (if required), rebevelling as required, radiography and other NDT examination, joint coating as per specification.Contractor shall supply of all consumables, manpower, machinaries, materials, N2 gas etc. and carry out all works as per the provisions of Contract document and instructions of Engineer-in-charge. | Item86
87 | For 12" NB | Item87 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
88 | PRE-COMMISSIONING AND ASSISTANCE IN COMMISSIONING OF PIPELINE SYSTEM Swabbing, drying, purging with nitrogen of the complete pipeline network and the associated facilities being installed to the specified acceptance criteria, carrying out pre-commissioning works, providing assistance during the complete duration of commissioning operations for entire pipeline network system including supply of all equipment, man-power, consumables (including pigs & nitrogen required for purging with maintaining nitrogen column of mininum 10% of pipeline geometric volume) materials for all temporary works and performing all associated works, complete as per the relevant specifications, other provisions of Contract document and instructions of Engineer-in-charge. | Item88
89 | For 12" NB Pipeline | Item89 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
90 | IDLE TIME PRESERVATION OF PIPELINE Preservation of complete pipeline and associated facilities forming part of the pipeline as per Bid document and its maintenance including supply of all consumables, all equipment, manpower, etc. complete as per the requirements of specifications, other provisions of Contract document and instructions of Engineer-in-charge. Note : Owner reserves the right to exercise either or none of the rates below. | Item90
91 | By filling and pressurizing with nitrogen to a pressure of 2 bar(g) for a period of 3 months. | Item91 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
92 | For 12" NB Pipeline | Item92 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
93 | For every additional period of one month or part thereof | Item93 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
94 | For 12" NB Pipeline | Item94 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
95 | RCC VALVE PITS All civil works including supply of all materials, excavation of pit, piping supports including all PCC and RCC works for valves pits including pedestals with insert plates as required sealing of pipe at valve pits, providing cover etc. and finishing , clean-up and restoration of site, filling and grading of area around valve station for avoiding any local flooding of area, as per typical drawing and specification enclosed and instructions of Engineer-in-charge. In this item, instead of Brick Work, RCC will be done | Item95 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
96 | Valve Pit of Size 2m x 2m | Item96 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
97 | SUPPLY OF ASSORTED PIPE, FITTINGS AND FLANGES Complete works of supply of pipes, flanges & fittings for aboveground & underground installation including all taxes, duties, transportation and inspection charges but not limited to, the following items in accordance with PMS (piping material specification), relevant specifications & drawings indicated in job specification under SCC (technical) and instructions of Engineer-in-charge and as per all provisions of the CONTRACT DOCUMENT. - Handling including lifting, transportation from Contractor Stores to CONTRACTOR's workshop for fabrication and/ or to work site for field fabrication and erection for all piping items supplied by Contractor. | Item97
98 | Carbon Steel Pipe (A 106, Seamless B-36.10/ API X 52 ) | Item98
99 | Size Rating/ Schedule | Item99 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
100 | 2" NB, BE Sch. 80 | Item100 | 55 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
101 | 1" NB, PE Sch. 80 | Item101 | 40 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
102 | ¾" NB, PE Sch. 160 | Item102 | 35 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
103 | Flanges | Item103
104 | Weld Neck (B-16.5, 300# A105,125 AARH, Serrated finish) | Item104
105 | Size Rating/ Schedule | Item105 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
106 | 2" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item106 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
107 | Blind Flanges (B-16.5, 300# A105,125 AARH Serrated) | Item107
108 | Size | Item108
109 | 2" NB, RF | Item109 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
110 | Elbow (Seamless) | Item110 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
111 | 90° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item111
112 | Size Rating/ Schedule | Item112
113 | 12" NB 300# | Item113 | 26 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
114 | 45° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item114 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
115 | Size Rating/ Schedule | Item115
116 | 12" NB 300# | Item116 | 24 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
117 | 90° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item117 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
118 | Size Rating/ Schedule | Item118
119 | 12" NB 300# | Item119 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
120 | 45° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item120
121 | Size Rating/ Schedule | Item121
122 | 12" NB 300# | Item122 | 22 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
123 | 22½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D) Min Thickness 6.4mm | Item123 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
124 | Size Rating/ Schedule | Item124
125 | 12" NB Sch. Std. | Item125 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
126 | 11½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D), Min Thickness 6.4mm | Item126
127 | Size Rating/ Schedule | Item127
128 | 12" NB 300# | Item128 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
129 | Tees (Seamless) | Item129
130 | Equal Tee (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item130
131 | Size Rating/ Schedule | Item131
132 | 12" NB x 12" NB x 12" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item132 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
133 | 2" NB x 2" NB x 2" NB Sch. XS | Item133 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
134 | Weldolet and Sockolet | Item134
135 | Weldolet (MOC A105 & DIM. MSS SP 97) | Item135
136 | Size Rating/ Schedule | Item136
137 | 12" NB x 2" NB Sch. 80. | Item137 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
138 | Sockolet (MOC A105 & DIM. MSS SP 97) | Item138
139 | 12" NB x 3/4" NB #6000 | Item139 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
140 | Butt Weld Disc End Cap (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item140
141 | Size Rating/ Schedule | Item141
142 | 12" Sch. Std. | Item142 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
143 | Fabrication & Installation of Underground Valve Assembly | Item143 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
144 | 12"NB Isolation Valve/tap-off assembly as per Drg. No. MNGL/Plng./Steel/40 | Item144 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
145 | Note: | Item145 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
146 | For all the supply items mentioned above, procurement shall be made as per enclosed Data Sheets and respective technical specification, after due approval of Engineer-in-charge. | Item146
147 | The quantities mentioned above are tentative and quantities for above supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item147
148 | PLANT PIPING (ABOVEGROUND) Fabrication and testing of carbon steel piping and fittings, valves, IJ, including supply of all consumables, equipment, manpower, and other resources and execution of job as per instruction AIC/EIC.Transportation of all piping items from Owner's and/ or Contractor's storage point to work at site/ workshop as applicable, complete work of fabrication, erection, painting, testing of pipes, flanges and fittings and making ready for further Commissioning / Start-up of carbon steel piping of all sizes and ratings including supply of all consumables, equipment, manpower and other resources and execution of, but not limited to, as per all provisions of the CONTRACT DOCUMENT. | Item148 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
149 | Fabrication including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site, cutting, edge preparation, inclusive of grinding the edges of pipes, fittings, flanges, reducers etc. to match with the matching edges of uneven thickness, wherever required, fit-up, welding of pipes and fittings like elbows, tees, reducers, weldolets, sockolets, Valves, IJ etc. flanges, vent and drain point connection, Radiography and NDT of all joints etc, including providing stubin connections, fabricated fittings and reinforcement pads etc., as required. | Item149 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
150 | Erection of pipes of all types and thickness at all elevations, connecting with equipment nozzle, aligning, installation and carrying out connected activities for all types of valves, all online instruments and fittings of all sizes of elbow, reducers, tees, flanges, blind flanges, spectacle blind flanges, branch connection / tapping for pressure gauges, including installation of gaskets and bolts. | Item150 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
151 | Erection including prior cleaning, lifting, placing on pipe sleepers and supports, overhead on racks, skids and at all elevations including installation and carrying out connected activities for all types of valves including supply and fixing of gaskets, studs/ bolts, nuts wherever required for all sizes, levelling, aligning, joining of flanges, blind flanges, connecting with equipment, nozzles, strainers, tie-in with existing piping/facilities, etc. tapping for inline instruments like pressure gauges, thermowells, sample connection, etc. | Item151
152 | Hydro testing of the piping job shall be conducted at pressure mentioned in specification for a period of 4 hours by using de-mineralised water, to check its strength. No visible leakages shall be detected during the test. Testing shall be conducted as per tender specification. | Item152
153 | Preparation of final bill of material based on piping GADs. | Item153
154 | Preparation of isometric and fabrication drawings. | Item154
155 | Carrying out Non-destructive testing as required | Item155
156 | Painting of entire system (including aboveground all pipes fittings, flanges and accessories) as per specifications suitable for highly corrosive area environment including supply of approved paints and primers, application of primer and paints, indentification lettering/ numbering, colour coding, etc. as specified including rub down & touch up of shop primer or scrapping of shop primer wherever required by COMPANY and providing scaffolding for all heights etc. | Item156
157 | Cleaning and flushing by water/ compressed air, testing of the systems including hydrostatic, pneumatic and any other type of testing as specified, draining, drying by compressed air/other methods approved by COMPANY. | Item157
158 | Precommissioning & making operational all piping system and equipments. | Item158 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
159 | Commissioning Contractor scope shall provide all necessary assistance in term of supply of man-power, equipment, tools and tackles required amount of nitrogen for purging of entire terminal piping system including equipments etc. to the company during commissioning activities. | Item159 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
160 | Completion of all such work in all respects as per scope of work and as per drawings, specifications and instructions of the COMPANY and keeping the system ready in all respects for further commissioning and start up. | Item160 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
161 | Hook-up works (with client/ consumer piping at battery limits): | Item161 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
162 | Complete Carbon Steel aboveground Piping Work with painting including all fittings, flanges and supply of all required gaskets, studs bolts & nuts etc. and Any other work and material required for the completion of the work and not covered above and desired by EIC shall be in the scope of contractor | Item162 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
163 | Carbon Steel Pipe (ASTM A 106, Seamless B-36.10 / API X 52) | Item163 | 150 | inch Dia |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
164 | 1) Pipe Specification and thickness may vary depending upon availability of pipe. No extra payment shall be made for this. 2) All butt welded fittings & flanges end shall generally match with connecting pipe wall thickness. However, in case of misalignment, Contractor shall have to do end preparation without any extra cost. 3) All o-lets less than 2" NB size, all sizes of coupling and nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under erection rate. | Item164 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
165 | Aboveground installation of Insulating Joint & Valves etc. Handling including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site and installation of all types of valves, insulating joint including assembly of valve accessories, (if any) by bolting, threading or welding, supply and insertion of gaskets, nuts & bolts, nipples, etc. at all elevations of pipe sleepers, supports or overhead on racks, equipments nozzle, skid & painting etc. supply of all consumables, manpower, equipment, etc. for completion of all works as per scope of work and as per drawings, specifications and instructions of Engineer-in-charge including servicing/ cleaning of valve wherever requried. | Item165 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
166 | 12" NB, 300# - Insulating Joints | Item166 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
167 | STRUCTURAL WORKS | Item167 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
168 | Supply of erection of single leaf mild steel gate 2.5m high with mesh upto 2m height and barbed wire fencing and 2m wide complete in all respect including painting as per TS on all MS items, all works as per specification and drawings excluding foundations and RCC beams. | Item168 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
169 | Supply of all materials, fabrication and erection of chain link fencing 2.5m high with mesh up to 2m height and barbed wire fenching complete in all respects including painting as per TS on all MS items, all works as per specification and drawings excluding foundation and RCC beams. | Item169 | 200 | RM |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
170 | Pipe Supports & Other Structures | Item170 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
171 | Supply, fabrication and erection of all types of pipe supports like clamps, saddle, guide stops, cradles, turn buckles, anchors, T-posts; stockade/ trestle and pipe bridge for overhead piping; frames for canopy, approach ladders and platforms, crossover, cable tray supports, etc. including painting suitable for highly corrosive area as per specification labour and supervision & complete work as per drawings, specifications and instruction of Engineerqw-incharge. (Bolts, nuts, washers, U-clamps etc. for supporting shall be supplied by the Contractor within the rates quoted. These items will not be measured and paid seperately). The work is to be completed in all respect as per scope of work and specification. | Item171 | 250 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
172 | Notes: | Item172 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
173 | The quantities indicated are estimated values and hence are approximate. Final payment will be made based on actual quantities to be certified by the Purchaser. | Item173
174 | The cost of MS bolts (permanent and service(, washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants etc., as required for the work shall be deemed to be included in the quoted rates. | Item174 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
175 | All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accrodance with time schedule, are deemed be included in the quoted rates. | Item175
176 | CIVIL WORKS | Item176
177 | Site Grading Excavation in earth and filling to the grades and levels shown in the approved drawings in all kinds of conditions including for Road embarkments, using approved quality good earth from designated borrow area, for all heights and depths including clearing and stripping (min. 150mm) of the area marked for filling, taking spot levels, consolidating the exposed natural soil surface, excavating the earth from borrow area loading, transporting & unloading, spreading in layers not exceeding 150mm thickness, breaking clods, watering (if reqd.), ramming and compacting by manual/ mechanical means to give minimum 92% of modified Proctor's density of earth, testing & dressing including disposal of all unserviceable material all complete as per specifications and directions of Engineer-in-charge. | Item177 | 200 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
178 | (Rate to include cost of all labour, tools, tackles, equipment, hire charges, cost of borrow earth by way of royalties, right of way, cess etc., as applicable with all bye works and sundry works). | Item178
179 | Plain Cement Concrete Supplying and laying plain cement concrete (including shuttering of required) in all types of concrete works including levelling courses below foundation, substructure, superstrcuture, chambers, cable tranch, under floors and any other locations, at all leveies as per drawings, specifications and directions of the Engineer-in-charge. | Item179
180 | PCC 1:2:4 1 Cement : 2 Coarse sand : 4 stone aggregate 20mm nominal size. | Item180 | 500 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
181 | Reinforced Cement Concrete Providing and laying reinforced cement of grade M-20 with 20mm and down grade crushed stone aggregate in all types of structures like foundations, pedestals, pedestal bases, pipe supports, sleepers cable trench inlcuding constrcution joints, bitumen painting on surface in contact with soil, providing and fixing reinforcing steel, shuttering, inserts, finishes etc. at all depths and heights complete as per drawings, specifications and direction of the Engineer-incharge. | Item181 | 400 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
182 | Rate to include cost of all labour, tools, tackles, equipment, hire charges, supply of all maerials such as minimum 43 grade cement including sulphate resistant cement for substructures, R/F steel, Inserts, bolts, conduits, bitumen, other minor constrcution materials, shuttering, stanging, earthwork in excavation and backfilling using serviceable earth in all conditions, shorting bailing and pumping out water, testing of concrete, curing etc. with all bye works and syndry works. | Item182
183 | TEMPORARY CATHODIC PROTECTION SYSTEM | Item183
184 | Design, detailed engineering, supply, installation, testing and commissioning of the temporary Cathodic protection system using Mg/ Zn galvanic anodes to protect the external surface of 3 LPE coated entire 5.5 km (approx.) long steel pipeline network against corrosion for design life of minimum 1 year or till commissioning of PCP system whichever is later as per standard specification No. MNGL/Steel/TS/15 for temporary cathodic protection system. Scope shall also include but not limited to the following for completion of jobs: | Item184 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
185 | Measurement of soil resistivity along the right of way of the main pipeline route as per specification for design & installation of anodes. | Item185
186 | Collection of additional data related to cathodic protection along the right of way of pipeline as per specifications. | Item186 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
187 | Supply, installation, testing & commissioning of one set of spark gap arrestor with 2 plate Zinc grounding cell of 20 kg net weight each across each insulating joint as per specification. | Item187
188 | Supply, installation, testing & commissioning one set of polarisation cell with zinc anode at all high tension (66KV or higher) electrical power transmission line/Equipment crossing or running parallel to the pipeline for grounding purpose as per specification. The rating shall depend upon anticipated fault current & ground bed resistance at the location of installation. However, the rating of polarisation cell (krick) shall not be less than 5 KA & number of 20 kg net weight zinc anode shall not be less than two. | Item188
189 | Supply & installation of Zinc Ribbon Anodes at 4-8 O’Clock position in the interval of 2 metre (max.) on carrier pipes at all cased crossings i.e. railways/ roads etc. | Item189 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
190 | Monitoring of the protection system for 6 months. | Item190
191 | All civil/ structural works related to TCP system including supply of bricks, cement & steel etc. required for completion of the system. | Item191 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
192 | For 12" | Item192 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
193 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item193 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
194 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item194 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
195 | FIELD INSTRUMENTATION | Item195 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
196 | PRESSURE INSTRUMENTS | Item196
197 | Supply , Installation of Pressure Gagues and their accessories inclusive of supply of necessary piping materials and tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/ manifolds & hydraulic testing (exclusive of calibration of instruments) as per installation standard attached elsewhere in Tender Document and Supply as per Data Sheet No.MEC/23K8/05/E5/I/001/DS-PG. Give breakup of supply and Installation rate. | Item197 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
198 | CALIBRATION | Item198
199 | Calibration of the instruments listed below including removal of instruments from pre-installed locations like panels, enclosure racks, fields etc. and refixing them back in respective/ required places, providing equipments, necessary test jigs, instrument air and all consumables. Calibration reports shall be prepared and to be submitted to the Purchaser/ Consultant. | Item199
200 | Pressure Gauges | Item200 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
201 | Note: | Item201 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
202 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item202 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
203 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item203 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
204 | PIPING WORKS FOR SECTIONALISING VALVE STATION-CUM-TAP-OFF POINT All works for fabriaction and installation of all piping above ground at all elevations and below ground at all depth for Sectionalising Valve Station alongwith preparation of construction drawings duly approved by EIC, in all type of terrains and soils including transportation and handling of all Owner supplied materials i.e. extended stem butt welded sectionalising gas actuated ball valve, other types of valves, line pipes for mainline, 4" NB pipe for all branch line including ventlines from Owner's designated place(s) of issue to work site. | Item204 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
205 | Contractor shall supply all required size & type of piping material like pipes, fittings & flanges etc. as per PMS alongwith 2" NB pipe for all branch line & vent line (wherever required) including supply of all consumables, manpower, machinaries, materials etc. and carrying out all mechanical works of underground and above ground piping including fabrication, welding, nondestructive testing of welds, weld repairs/ retesting, cleaning/ flushing, pre-hydrotesting & hydrostatic testing, dewatering, functional testing, cutting of mainline and bevelling (if required) | Item205
206 | assembly, including radiography of tie-in joints, corrosion, coating and external painting as required, installation of instruments like pressure/ temperature instruments/ gauges alongwith complete SS Tubing works including supply of SS Tube and thier accessories etc., as required, obtaining all statutory clearances, approvals and permissions for the works (wherever required), making of valve pit (for detail refer relevant drawings) for SV Stationscum- tap-off points enclosed with tender filled with sand, excavation and filling in all types of soils including soft/ hard rock for installation of piping/ pipe supports providing pipe supports, area fencing and gate including all associated civil and structural works; painting, finishing, clean-up and restoration of site; preparation of as-built drawings, documents and project records and performing all works as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge. In this item, instead of Brick Work RCC will be done | Item206 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
207 | Type - I SV Station on 12" Pipeline | Item207 | 1 | Lumpsum for each |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
208 | Note: i) Work under above items are exclusive of all works associated with main pipeline covered under Item No. 1.0 above. ii) All civil/ structural works including area fencing and gate, valve pits except for piping support will be paid separately as per unit rate provided elsewhere in the SOR. iii) All coupling, nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under above item rate. | Item208 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
Total in Figures | [51 empty] | 0 | 0 | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## BoQ11 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR | [49 empty] | 1
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Maharastra Natural Gas Ltd.,Pune
Name of Work: TENDER FOR LAYING & CONSTRUCTION OF 12” NB X 6 KM U/G STEEL PIPELINE NETWORK & ASSOCIATED WORKS FROM NEAR HOTEL SAMRUDDHI, TALEGAON ON NH 548C TO NEAR NYARA PUMP, DHOKSAL AT NH 548C (Section No-11)
Tender No: MNGL/CP/2024-25/109
Do you want to quote for this sheet ? |  |  | Yes
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE / SCHEDULE OF RATES (SOR) (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Rate inclusive of all taxes and duties except Goods & Service Tax (Rs.) | Per Unit Goods & Service Tax (GST) In % (To be entered by the Bidder) | GST in Rs. | Unit rate inclusive of all taxes & duties including GST (Rs.) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | CARBON STEEL PIPES | Item1
2 | PIPELINE LAYING / INSTALLATION in all type of surface (Normal/built-up surface) "Receiving and taking over" as defined in the specifications, handing, loading, transportation and unloading of Owner supplied 3-Layer PE coated linepipes from Owner's designated stack-yard to Contractor's stock yard/workshop/work-site including preliminary activities, preparation of drawings, wherever required for crossing etc. including handling, stacking, stringing on the pipeline Right-of-Use/ pipeline route alignment, carrying out inspection of company supplied materials including linepipes at the time of taking over, laying/ installation of coated linepipes, associated burried valves, barred tees, insulating joints, flanges & fittings of all sizes, thickness & ANSI class rating and accessories as per specification wherever required depending on site condition including execution of all works, "taking over", handling , including loading and unloading, transportation of Owner supplied materials other than linepipe from Owner's designated place (s) of issue to work site, | Item2 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3 | additional lands required for Contractor's storage, fabrication, access for construction, procurement and supply of all materials (except Owner supplied materials), consumables, equipment, labour and other inputs, carrying out all temporary, ancillary, auxiliary works, aquistion of ROU/ROW for laying of pipeline from HDD Exit and entry point to Tie in Point of existing Pipeline/ ROU, ready for commissioning of pipeline as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge, including but not limited to carrying out the following works: | Item3 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4 | Surveying of route and detours required at the time of execution including marking the same in topographical sheet, preparation of construction drawings showing survey details, and submit same to Owner for review / approval. | Item4
5 | Staking and installation of construction markers, clearing, fencing, grubbing, cutting of trees, full filling all the requirements of various statutory/ environment authorities to the entire satisfaction of concerned authorities, grading of work area. Shifting of all obstruction within the ROU/ Pipeline route alignment viz. electrical lines/ poles, telephone line / poles, etc. coordination with concerned authorities and obtain permissions from these authorities. | Item5
6 | Trenching to all depths by excavation in all types of soils including soft/ hard rock and different type of pavement / footpath / roads etc. including rock breaking, chiselling or otherwise cutting etc. as required and storing excavated soil, reusable materials at designated area as directed by Engineer in charge and to a width to accommodate the Steel pipeline as per the relevant standard/ specification etc. [The minimum depth of the top of pipeline shall be 1.2m measured from top of pipeline coating to the top of undisturbed surface of the soil or as per SCC/ OISD - 141 / 226, whichever is higher]. Dewater of trenches if required as per site condition. | Item6
7 | Carrying out repairs of pipe defects/ replacement in case of irreparable defects and repairs of defects of pipe coating not attributable to Owner including defects/ damages occurring during transportation / handling. | Item7
8 | Stringing of line pipes along pipeline trench / ROU on straw / sand / soft soil bags including supply of bags and its filling materials. | Item8
9 | Checking, cleaning, aligning, bending, cutting and bevelling (as required) of pipes for welding and field adjustments including pipe fittings, welding, carrying out non-destructive testing of welds as required including 100% radiography by X-ray and providing all requisite equipment, labour, supervision, materials, films, consumables, all facilities and personnel to process, develop, examine and interpret radiographs and other tests as required, carrying out repairs of weld joints found defective by Engineer-in-Charge, carrying out re-radiography and other tests as required on repaired joints. | Item9
10 | Carrying out installation of carrier line pipe at all minor crossing viz. carttrack, pathway, water bodies etc. at designated depth by open cut (except at crossing by HDD method). | Item10
11 | Carrying out installation of carrier line pipe in the casing pipe at cased crossing (excluding installation of casing pipes which is covered separately). | Item11
12 | Coating of field weld joints, long radius bends (R=3D), elbows, buried fittings and valves etc. including supply of coating materials etc. (i.e. heat shrinkable sleeves and high build epoxy etc.) as per PJS & Technical Specification compatible with 3 layer PE coating material of the line pipe. | Item12 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
13 | Counting the number and type of trees cut in presence of DFO/concerned authorities and keeping record thereof, stacking and handing over of all cut tress. | Item13
14 | Installation / lowering the pipeline in trench to required depth as per PJS, Techanical Specification & drawings, supply & placement of 1.0mm thk. HDPE Yellow colour warning mat,RCC tiles (300 mm width x 50 mm thick) over the pipeline in same trench along the complete route as per standard drawings, data sheets & technical specifications, padding around pipeline as per Standard Drg. no. MNGL/Plng./Steel/03 with suitable soil duly approved by EIC including supply of padding material, backfilling and its compaction to the satisfaction of concerned authorities with excavated earth / borrowed select soil including supply of borrowed select soil duly approved by EIC before backfilling and make ready for restoration to be done by Onwer / concerned authorities. | Item14
15 | Supply and installation of slope breakers, wherever required or, as directed by Onwer / Engineer–in–charge. | Item15
16 | Crossing the all-foreign pipeline / HT line / cable / any other utilities etc. with necessary concrete / HDPE sheet protection including coordination with all agencies and obtaining NOC | Item16
17 | Supply and installation of bank protection alongwith backfill materials duly approved by EIC for pipeline trench and banks falls under minor water body crossing as per technical specification & Std. Drg. No. MNGL/Plng./Steel/28, wherever required or, as directed by Onwer / EIC. | Item17
18 | Training and diversions of streams in steep slope area, wherever required. | Item18
19 | Carrying out air cleaning, pigging, flushing, cleaning and hydrostatic testing of complete pipeline with required quantity of corrosion inhibitor including pre-testing of designated sections complete as per specification and approved by Engineer–in–charge to specified pressures indicated elsewhere and duration after stabilization as per specification, providing all equipment, pumps, fittings, instruments, dead weight tester, pressure recorder, thermocouples etc., and services, supervision, labour, consumables, water including supply of corrosion inhibitor, air, etc. as required, locating of leaks and rectification of defect attributable to Contractor (rectification of defects in linepipe material not attributable to contractor shall be paid separately as per other item of schedule of rate), re-testing after rectification, dewatering after successful completion of hydrotesting of entire section and as per specification | Item19
20 | All tieing-in, including the tie-in(s) of the pipeline with the adjacent sections of pipeline including cutting of test header, rebevelling as required, radiography and other NDT examination, joint coating as per specification. | Item20
21 | Final clean-up of right-of-use or area disturbed by contractor during their construction activities for laying of pipeline works and disposal of debris and surplus material to designated disposal areas and backfilling of trench and compaction of the same as per satisfaction of Owner and / Or as directed by Engineer–in–charge. | Item21
22 | Installation of all burried valves (except extended stem valves) inside the valve pit and making provision to operate the valve. | Item22 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
23 | Preparation of as-built drawings, pipe-books (1 set of tracing on polyester film and 6 sets of as-built drawings and 1 soft copy and 6 hard copies of pipe book) All the works shall be executed in accordance with the provision of contract including carrying out all temporary/ ancillary/ auxiliary works required for the performance of the works and all other acts, deeds, matters and things necessary to make the pipeline ready for precommissioning activities. | Item23 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
24 | Raking up of hard surface of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. Payment for cutting of hard rock, if any, is covered unders SOR no. 76 | Item24 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
25 | Specified dia Thk (mm) Material Coating Type Length of each pipe (mm) NB | Item25 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
26 | 305 (approx.) 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item26 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
27 | Note: This item shall be applicable for the underground steel grid main pipeline & branch pipeline, barred tees, insulating joints, bends, flanges & fittings, accessories etc. (i.e. including arrangement for making provision for tap-off on proposed steel grid main pipeline) and aboveground approach pipeline upto Insulating Joint (excluding installation of aboveground insulating joint) for various stations. | Item27
28 | Items except above are covered separately. The lengths of pipelines are tentative. | Item28 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
29 | Permission Liasioning /Follow-up | Item29 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
30 | Liasioning & follow up for Permission with all the concerned authorities & boards viz Railways, NH, PWD, MIDC, Local Municipal, Panchyat, Electricity, REC, RES, Sewage water, Drinking water, Forest, Social Forestry, Owners of OFC, Traffic, Law & Order, Fire Brigade, Private Land Owner etc. for entire pipeline length and associated terminals (like SVs, tap-offs) alongwith associated work as per tender. | Item30 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
31 | Laying of RCC Tiles | Item31 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
32 | Providing single layer of RCC Tiles with supply of RCC Tiles to entire width of trench above Warning Mat placed in trench over the laid pipeline as per standard drawing, specification and instruction of Owner. (Rate to include cost of all labour, tools, tackles, equipment, hire charges & supply of all materials, etc.) | Item32
33 | For width of 12" pipeline trench | Item33 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
34 | Barricading to comply with HSSE | Item34 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
35 | Steel barricading of the trenches Cautionary Sign Boards and lighting arrangement shall be provided as per attched drawing no.MNGL/Plng./steel/04. The rates include barricading of trenches along with sign boards, lighting etc. and maintain the same till the back filling of the trench. Rates will be payable per metre of BARRICADING PROVIDED. If proper barricading is not provided, MNGL will barricade the trenches at the risks and costs of the CONTRACTOR and will levy penalty of twice the rate per unit for the relevant section of the pipeline apart from other actions as per contract. | Item35 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
36 | RESTORATION OF ROADS Restoration of asphalt / concrete / red stone roads / pavement/Footpath/Paver block including compaction of soil, to original condition as per requirement and to the entire satisfaction of EIC and / or concerned Owners having jurisdiction for following thickness. | Item36 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
37 | Restoration of Asphalt road upto 10 cm thickness | Item37 | 600 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
38 | Restoration of Asphalt road beyond 10 cm upto 20 cm thickness | Item38 | 200 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
39 | Restoration of Concrete road upto 10 cm thickness | Item39 | 600 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
40 | Restoration of red stone road / footpath / pavement/ Paverblock upto 4 cm thickness | Item40 | 500 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
41 | BORROWED SELECT SOIL FOR BACKFILLING Additional work over and above item 1.0 for supply of specified and approved quality of borrowed soft graded soil / sand in place of available excavated material and / or other suitable soil as per applicable standards / specifications, including backfilling of excavated trench for specified length after laying and padding of pipeline, including transportation of such special backfill material over all distances, complete. | Item41 | 900 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
42 | CROSSING OF STEEL PIPELINE BY OPEN CUT | Item42
43 | Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insatllation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed. | Item43
44 | Road Crossing By Open Cut Method Road Crossings at various locations by Open cut Method as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item44 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
45 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method | Item45 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
46 | Water body Crossing By Open Cut Method water/ canal/ nallah/ drain/ channel Crossings at various locations by Open cut Method as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item46 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
47 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method | Item47 | 90 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
48 | Note: Laying of the pipeline by the approved method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item48
49 | Backfilling of the Road/water/ canal/ nallah/ drain/ channel Crossings/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority. | Item49
50 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item50 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
51 | CROSSINGS/LAYING ALONG THE ROAD BY HDD METHOD | Item51
52 | Complete work of the any crossing (between the limits are defined as approved drawings) by HDD method including "Receiving and taking over" owner supplied three layer PE coated line pipes from Owner's designated place to issue/ dump site(s) and transportation to Contractor's stock yard/ work shop/ work site including all handling loading, unloading, aligning etc. supply of all Contractor supplied material, manpower, equipment, other resources and aquiring the required land for storage, fabrication inclduing string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type Heat Shrink Sleeve and repair of pipeline coating with special repair patch materials as per specification,pre-testing etc. of complete string made for crossing access for Contractor etc and execution of, but not limited to, following works in accordance with specifications scope of work and instructions of Engineer-in-charge and as per all provision of Contract Document. | Item52
53 | Pre-construction surveys based on site visit, collection of historical data from irrigation/ concerned department including design & calculation and detail engineering and making of crossing drawing for getting their approval from concerned Authority/ Engineer-in-charge, getting work permit/ NOC for water crossings/ road crossings as well as utility crossings (if any) encountered during crossing prior to start the execution of work. | Item53 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
54 | Directional drilling to required depth from top of road including maintenance of drill hole in all types of strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) at all depth to accommodate the pipeline at all conditions encountered during rail/ road crossing by approved HDD methods for providing minimum cover specified in code/ specification or the actual depth as decided by concerned authority, whichever is more. | Item54 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
55 | In case of water crossing, drilling to the required depth on the banks and bed including maintenance of drill hole in all types of soil strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) all depth to accommodate the pipeline a by HDD methods for providing with minimum cover over top of the pipe at all point across the maximum possible width of water bed (as per drawing) either 1.5 mtrs. below the predicted scour profile expected during the life time of the pipeline or 2.5 mtrs. below the available lowest firm bed (if scour profile/ depth not available) of the water crossing by ascertaining bed level upto 50 mtrs. both the side from crossing location or the actual depth as decided by concerned Authority/ Engineer-in-charge whichever is more. | Item55 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
56 | Laying of the pipeline by the approved HDD method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints with special type Dirax Heat Shrink Sleeve or equivalent and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item56 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
57 | Backfilling of the ditch/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority and all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specification, approved drawings, calculations, methods and to the satisfaction of Engineer-in-charge and/or as directed by concerned Authority. | Item57 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
58 | Post installation hydrotest dewatering and tie-in with pipeline at either side of crossing/banks etc. | Item58 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
59 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item59 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
60 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 by HDD Method . | Item60 | 120 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
61 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item61 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
62 | Installation of carrier pipes by rock drilling for Road/water/Canal/ nallah/ drain/ channel/along the road, or wherever required in all types of hard rock. It includes survey of the underground utilities, submission of profile for approval, execution of the work as per the standard procedure, including , excavation of the pits, insertion/pulling of the carrier pipe, removal of malba, subsequent backfilling and restoration of the facility crossed as per original condition, including supply of all other materials, equipment, consumables, manpower etc including string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type of Heat Shrink Sleeve (Direx) and repair of pipeline coating with special repair patch materials as per Specification, pre-testing etc. of complete string made for crossing/ laying access for Contractor etc. and execution of, but not limited to, following works in accordance with specifications and instruction of Engineer-in-Charge and as per all provision of Contract Document. Balance activities as defined in SOR Item of open trench. Note:The length of HDD mentioned is tentative and may vary to the considerable extent depending upon requirements as per site conditions. The length mentioned in SOR is indicative for all the crossing to be done by HDD, numbers and locations shall be decided by Engineer-in-Charge depending upon site condition. Payment for the length of final tie-in carrier pipeline string with mainline laid by HDD are inclusive in this above item rate. No separate payment shall be made under other clauses mentioned elsewhere. Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item62
63 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 by HDD Method . | Item63 | 140 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
64 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item64 | 90 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
65 | Note: (i) Crossing width & Actual string length for HDD shall vary as per design calculations & site condition so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. | Item65
66 | (ii)Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item66
67 | (iii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by HDD method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item67
68 | (iv) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossing at different locations. | Item68
69 | (v) The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. | Item69
70 | Note: (i) Quantity mentioned under item nos. 44, 46 are indicative only for different location of roads/water/ canal/ nallah/ drain/ channel Crossings. (ii) Actual length & width of individual crossing and cover from top of casing pipe/ carrier pipe string may vary depending upon site condition, approved crossing drawings, specifications etc. and / or as decided by Engineer-in-charge/ Concerned Authority. | Item70
71 | (iii) Payment for supply & installation of Zinc ribbon anode and its design excluded from above item and covered elsewhere in the SOR. (iv) Payment for the length carrier pipeline string inserted in casing pipe laid by Boring are covered separately and shall be paid under other clauses mentioned elesewhere in the SOR. | Item71
72 | Excavation beyond 1.5m depth in case of crossing of utilities/ drain/ culverts etc. through open cut upto the following depth (including restoration of the damaged area to its original condition and satisfaction of the Engineer-in-charge / concerned authorities) : - | Item72 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
73 | In all type of surface (Kachha/ built-up surface / Hard surface) of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. The other activities are as per SOR 1.1. Payment for cutting of hard rock, if any, is covered unders SOR no. 76 | Item73
74 | Deeper than 1.5 m & upto 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item74 | 700 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
75 | Deeper than 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item75 | 300 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
76 | Excavation of hard rock | Item76
77 | Excavation of hard rock wherever hard rock of single piece exceeding 1.0 m in length removable by pneumatic chisel/ drill as per direction of EIC. | Item77 | 3800 | Cub. M |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
78 | REPAIR OF COATING DEFECTS (NOT ATTRIBUTED TO CONTRACTOR) | Item78
79 | Repair of Holiday in Coating (Noted and recorded at the time of "receiving and taking over") Supply of all coating repair materials as per requirements of specification to be compatible with line pipe coating material, supply of all consumables, utilities, equipments and all manpower required, pipe cleaning and surface preparation, repairing of coating defects (resulting in holiday) and testing including all handling, transportation, etc. for line pipes, performing all works necessary for the completion of the works stirctly in accordance with relevant specification and instructions of Engineer-In-Charge. This rate shall be applicable per sq. cm of the exposed steel area exposed steel area. | Item79 | 2200 | Sq. cm. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
80 | PERMANENT MARKERS Supply, fabrication and installation of all types of permanent markers along the route including all associated civil works such as excavation in all types of soil, construction in all types of soil, construction of pedestals and grouting with concrete, clearing, supply and application of approved colour and quality of primer and paint, stencil letter cutting for numbers, direction, change etc., restoration of area to original condition and performing all works as per drawing, specification and instruction of engineer-in-charge. | Item80
81 | Pipeline RCC boundary / route marker as per drawing | Item81 | 120 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
82 | Pipeline warning markers with post & foundations | Item82 | 40 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
83 | Pipeline direction marker with post & foundations | Item83 | 25 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
84 | Pipeline KM with post & foundations | Item84 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
85 | HOOK -UP | Item85
86 | Hook-up of proposed pipeline by welding of final tie-in-joint with any existing laid pipeline portion of river X-ing ,existing Tap-off & battery limit of section IV including Hook-up point of the existing pipeline to be made ready for welding by cutting of flanges / valves / headers at all depth in all type of soil etc. Venting of N2 / gas / gas mixture as required purging of N2 Gas (if required), rebevelling as required, radiography and other NDT examination, joint coating as per specification.Contractor shall supply of all consumables, manpower, machinaries, materials, N2 gas etc. and carry out all works as per the provisions of Contract document and instructions of Engineer-in-charge. | Item86
87 | For 12" NB | Item87 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
88 | PRE-COMMISSIONING AND ASSISTANCE IN COMMISSIONING OF PIPELINE SYSTEM Swabbing, drying, purging with nitrogen of the complete pipeline network and the associated facilities being installed to the specified acceptance criteria, carrying out pre-commissioning works, providing assistance during the complete duration of commissioning operations for entire pipeline network system including supply of all equipment, man-power, consumables (including pigs & nitrogen required for purging with maintaining nitrogen column of mininum 10% of pipeline geometric volume) materials for all temporary works and performing all associated works, complete as per the relevant specifications, other provisions of Contract document and instructions of Engineer-in-charge. | Item88
89 | For 12" NB Pipeline | Item89 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
90 | IDLE TIME PRESERVATION OF PIPELINE Preservation of complete pipeline and associated facilities forming part of the pipeline as per Bid document and its maintenance including supply of all consumables, all equipment, manpower, etc. complete as per the requirements of specifications, other provisions of Contract document and instructions of Engineer-in-charge. Note : Owner reserves the right to exercise either or none of the rates below. | Item90
91 | By filling and pressurizing with nitrogen to a pressure of 2 bar(g) for a period of 3 months. | Item91 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
92 | For 12" NB Pipeline | Item92 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
93 | For every additional period of one month or part thereof | Item93 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
94 | For 12" NB Pipeline | Item94 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
95 | RCC VALVE PITS All civil works including supply of all materials, excavation of pit, piping supports including all PCC and RCC works for valves pits including pedestals with insert plates as required sealing of pipe at valve pits, providing cover etc. and finishing , clean-up and restoration of site, filling and grading of area around valve station for avoiding any local flooding of area, as per typical drawing and specification enclosed and instructions of Engineer-in-charge. In this item, instead of Brick Work, RCC will be done | Item95 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
96 | Valve Pit of Size 2m x 2m | Item96 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
97 | SUPPLY OF ASSORTED PIPE, FITTINGS AND FLANGES Complete works of supply of pipes, flanges & fittings for aboveground & underground installation including all taxes, duties, transportation and inspection charges but not limited to, the following items in accordance with PMS (piping material specification), relevant specifications & drawings indicated in job specification under SCC (technical) and instructions of Engineer-in-charge and as per all provisions of the CONTRACT DOCUMENT. - Handling including lifting, transportation from Contractor Stores to CONTRACTOR's workshop for fabrication and/ or to work site for field fabrication and erection for all piping items supplied by Contractor. | Item97
98 | Carbon Steel Pipe (A 106, Seamless B-36.10/ API X 52 ) | Item98
99 | Size Rating/ Schedule | Item99 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
100 | 2" NB, BE Sch. 80 | Item100 | 55 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
101 | 1" NB, PE Sch. 80 | Item101 | 42 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
102 | ¾" NB, PE Sch. 160 | Item102 | 34 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
103 | Flanges | Item103
104 | Weld Neck (B-16.5, 300# A105,125 AARH, Serrated finish) | Item104
105 | Size Rating/ Schedule | Item105 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
106 | 2" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item106 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
107 | Blind Flanges (B-16.5, 300# A105,125 AARH Serrated) | Item107
108 | Size | Item108
109 | 2" NB, RF | Item109 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
110 | Elbow (Seamless) | Item110 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
111 | 90° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item111
112 | Size Rating/ Schedule | Item112
113 | 12" NB 300# | Item113 | 26 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
114 | 45° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item114 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
115 | Size Rating/ Schedule | Item115
116 | 12" NB 300# | Item116 | 24 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
117 | 90° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item117 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
118 | Size Rating/ Schedule | Item118
119 | 12" NB 300# | Item119 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
120 | 45° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item120
121 | Size Rating/ Schedule | Item121
122 | 12" NB 300# | Item122 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
123 | 22½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D) Min Thickness 6.4mm | Item123 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
124 | Size Rating/ Schedule | Item124
125 | 12" NB Sch. Std. | Item125 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
126 | 11½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D), Min Thickness 6.4mm | Item126
127 | Size Rating/ Schedule | Item127
128 | 12" NB 300# | Item128 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
129 | Tees (Seamless) | Item129
130 | Equal Tee (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item130
131 | Size Rating/ Schedule | Item131
132 | 12" NB x 12" NB x 12" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item132 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
133 | 2" NB x 2" NB x 2" NB Sch. XS | Item133 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
134 | Weldolet and Sockolet | Item134
135 | Weldolet (MOC A105 & DIM. MSS SP 97) | Item135
136 | Size Rating/ Schedule | Item136
137 | 12" NB x 2" NB Sch. 80. | Item137 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
138 | Sockolet (MOC A105 & DIM. MSS SP 97) | Item138
139 | 12" NB x 3/4" NB #6000 | Item139 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
140 | Butt Weld Disc End Cap (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item140
141 | Size Rating/ Schedule | Item141
142 | 12" Sch. Std. | Item142 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
143 | Fabrication & Installation of Underground Valve Assembly | Item143 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
144 | 12"NB Isolation Valve/tap-off assembly as per Drg. No. MNGL/Plng./Steel/40 | Item144 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
145 | Note: | Item145 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
146 | For all the supply items mentioned above, procurement shall be made as per enclosed Data Sheets and respective technical specification, after due approval of Engineer-in-charge. | Item146
147 | The quantities mentioned above are tentative and quantities for above supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item147
148 | PLANT PIPING (ABOVEGROUND) Fabrication and testing of carbon steel piping and fittings, valves, IJ, including supply of all consumables, equipment, manpower, and other resources and execution of job as per instruction AIC/EIC.Transportation of all piping items from Owner's and/ or Contractor's storage point to work at site/ workshop as applicable, complete work of fabrication, erection, painting, testing of pipes, flanges and fittings and making ready for further Commissioning / Start-up of carbon steel piping of all sizes and ratings including supply of all consumables, equipment, manpower and other resources and execution of, but not limited to, as per all provisions of the CONTRACT DOCUMENT. | Item148 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
149 | Fabrication including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site, cutting, edge preparation, inclusive of grinding the edges of pipes, fittings, flanges, reducers etc. to match with the matching edges of uneven thickness, wherever required, fit-up, welding of pipes and fittings like elbows, tees, reducers, weldolets, sockolets, Valves, IJ etc. flanges, vent and drain point connection, Radiography and NDT of all joints etc, including providing stubin connections, fabricated fittings and reinforcement pads etc., as required. | Item149 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
150 | Erection of pipes of all types and thickness at all elevations, connecting with equipment nozzle, aligning, installation and carrying out connected activities for all types of valves, all online instruments and fittings of all sizes of elbow, reducers, tees, flanges, blind flanges, spectacle blind flanges, branch connection / tapping for pressure gauges, including installation of gaskets and bolts. | Item150 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
151 | Erection including prior cleaning, lifting, placing on pipe sleepers and supports, overhead on racks, skids and at all elevations including installation and carrying out connected activities for all types of valves including supply and fixing of gaskets, studs/ bolts, nuts wherever required for all sizes, levelling, aligning, joining of flanges, blind flanges, connecting with equipment, nozzles, strainers, tie-in with existing piping/facilities, etc. tapping for inline instruments like pressure gauges, thermowells, sample connection, etc. | Item151
152 | Hydro testing of the piping job shall be conducted at pressure mentioned in specification for a period of 4 hours by using de-mineralised water, to check its strength. No visible leakages shall be detected during the test. Testing shall be conducted as per tender specification. | Item152
153 | Preparation of final bill of material based on piping GADs. | Item153
154 | Preparation of isometric and fabrication drawings. | Item154
155 | Carrying out Non-destructive testing as required | Item155
156 | Painting of entire system (including aboveground all pipes fittings, flanges and accessories) as per specifications suitable for highly corrosive area environment including supply of approved paints and primers, application of primer and paints, indentification lettering/ numbering, colour coding, etc. as specified including rub down & touch up of shop primer or scrapping of shop primer wherever required by COMPANY and providing scaffolding for all heights etc. | Item156
157 | Cleaning and flushing by water/ compressed air, testing of the systems including hydrostatic, pneumatic and any other type of testing as specified, draining, drying by compressed air/other methods approved by COMPANY. | Item157
158 | Precommissioning & making operational all piping system and equipments. | Item158 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
159 | Commissioning Contractor scope shall provide all necessary assistance in term of supply of man-power, equipment, tools and tackles required amount of nitrogen for purging of entire terminal piping system including equipments etc. to the company during commissioning activities. | Item159 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
160 | Completion of all such work in all respects as per scope of work and as per drawings, specifications and instructions of the COMPANY and keeping the system ready in all respects for further commissioning and start up. | Item160 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
161 | Hook-up works (with client/ consumer piping at battery limits): | Item161 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
162 | Complete Carbon Steel aboveground Piping Work with painting including all fittings, flanges and supply of all required gaskets, studs bolts & nuts etc. and Any other work and material required for the completion of the work and not covered above and desired by EIC shall be in the scope of contractor | Item162 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
163 | Carbon Steel Pipe (ASTM A 106, Seamless B-36.10 / API X 52) | Item163 | 150 | inch Dia |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
164 | 1) Pipe Specification and thickness may vary depending upon availability of pipe. No extra payment shall be made for this. 2) All butt welded fittings & flanges end shall generally match with connecting pipe wall thickness. However, in case of misalignment, Contractor shall have to do end preparation without any extra cost. 3) All o-lets less than 2" NB size, all sizes of coupling and nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under erection rate. | Item164 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
165 | Aboveground installation of Insulating Joint & Valves etc. Handling including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site and installation of all types of valves, insulating joint including assembly of valve accessories, (if any) by bolting, threading or welding, supply and insertion of gaskets, nuts & bolts, nipples, etc. at all elevations of pipe sleepers, supports or overhead on racks, equipments nozzle, skid & painting etc. supply of all consumables, manpower, equipment, etc. for completion of all works as per scope of work and as per drawings, specifications and instructions of Engineer-in-charge including servicing/ cleaning of valve wherever requried. | Item165 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
166 | 12" NB, 300# - Insulating Joints | Item166 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
167 | STRUCTURAL WORKS | Item167 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
168 | Supply of erection of single leaf mild steel gate 2.5m high with mesh upto 2m height and barbed wire fencing and 2m wide complete in all respect including painting as per TS on all MS items, all works as per specification and drawings excluding foundations and RCC beams. | Item168 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
169 | Supply of all materials, fabrication and erection of chain link fencing 2.5m high with mesh up to 2m height and barbed wire fenching complete in all respects including painting as per TS on all MS items, all works as per specification and drawings excluding foundation and RCC beams. | Item169 | 200 | RM |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
170 | Pipe Supports & Other Structures | Item170 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
171 | Supply, fabrication and erection of all types of pipe supports like clamps, saddle, guide stops, cradles, turn buckles, anchors, T-posts; stockade/ trestle and pipe bridge for overhead piping; frames for canopy, approach ladders and platforms, crossover, cable tray supports, etc. including painting suitable for highly corrosive area as per specification labour and supervision & complete work as per drawings, specifications and instruction of Engineerqw-incharge. (Bolts, nuts, washers, U-clamps etc. for supporting shall be supplied by the Contractor within the rates quoted. These items will not be measured and paid seperately). The work is to be completed in all respect as per scope of work and specification. | Item171 | 150 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
172 | Notes: | Item172 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
173 | The quantities indicated are estimated values and hence are approximate. Final payment will be made based on actual quantities to be certified by the Purchaser. | Item173
174 | The cost of MS bolts (permanent and service(, washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants etc., as required for the work shall be deemed to be included in the quoted rates. | Item174 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
175 | All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accrodance with time schedule, are deemed be included in the quoted rates. | Item175
176 | CIVIL WORKS | Item176
177 | Site Grading Excavation in earth and filling to the grades and levels shown in the approved drawings in all kinds of conditions including for Road embarkments, using approved quality good earth from designated borrow area, for all heights and depths including clearing and stripping (min. 150mm) of the area marked for filling, taking spot levels, consolidating the exposed natural soil surface, excavating the earth from borrow area loading, transporting & unloading, spreading in layers not exceeding 150mm thickness, breaking clods, watering (if reqd.), ramming and compacting by manual/ mechanical means to give minimum 92% of modified Proctor's density of earth, testing & dressing including disposal of all unserviceable material all complete as per specifications and directions of Engineer-in-charge. | Item177 | 200 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
178 | (Rate to include cost of all labour, tools, tackles, equipment, hire charges, cost of borrow earth by way of royalties, right of way, cess etc., as applicable with all bye works and sundry works). | Item178
179 | Plain Cement Concrete Supplying and laying plain cement concrete (including shuttering of required) in all types of concrete works including levelling courses below foundation, substructure, superstrcuture, chambers, cable tranch, under floors and any other locations, at all leveies as per drawings, specifications and directions of the Engineer-in-charge. | Item179
180 | PCC 1:2:4 1 Cement : 2 Coarse sand : 4 stone aggregate 20mm nominal size. | Item180 | 500 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
181 | Reinforced Cement Concrete Providing and laying reinforced cement of grade M-20 with 20mm and down grade crushed stone aggregate in all types of structures like foundations, pedestals, pedestal bases, pipe supports, sleepers cable trench inlcuding constrcution joints, bitumen painting on surface in contact with soil, providing and fixing reinforcing steel, shuttering, inserts, finishes etc. at all depths and heights complete as per drawings, specifications and direction of the Engineer-incharge. | Item181 | 400 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
182 | Rate to include cost of all labour, tools, tackles, equipment, hire charges, supply of all maerials such as minimum 43 grade cement including sulphate resistant cement for substructures, R/F steel, Inserts, bolts, conduits, bitumen, other minor constrcution materials, shuttering, stanging, earthwork in excavation and backfilling using serviceable earth in all conditions, shorting bailing and pumping out water, testing of concrete, curing etc. with all bye works and syndry works. | Item182
183 | TEMPORARY CATHODIC PROTECTION SYSTEM | Item183
184 | Design, detailed engineering, supply, installation, testing and commissioning of the temporary Cathodic protection system using Mg/ Zn galvanic anodes to protect the external surface of 3 LPE coated entire 5.5 km (approx.) long steel pipeline network against corrosion for design life of minimum 1 year or till commissioning of PCP system whichever is later as per standard specification No. MNGL/Steel/TS/15 for temporary cathodic protection system. Scope shall also include but not limited to the following for completion of jobs: | Item184 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
185 | Measurement of soil resistivity along the right of way of the main pipeline route as per specification for design & installation of anodes. | Item185
186 | Collection of additional data related to cathodic protection along the right of way of pipeline as per specifications. | Item186 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
187 | Supply, installation, testing & commissioning of one set of spark gap arrestor with 2 plate Zinc grounding cell of 20 kg net weight each across each insulating joint as per specification. | Item187
188 | Supply, installation, testing & commissioning one set of polarisation cell with zinc anode at all high tension (66KV or higher) electrical power transmission line/Equipment crossing or running parallel to the pipeline for grounding purpose as per specification. The rating shall depend upon anticipated fault current & ground bed resistance at the location of installation. However, the rating of polarisation cell (krick) shall not be less than 5 KA & number of 20 kg net weight zinc anode shall not be less than two. | Item188
189 | Supply & installation of Zinc Ribbon Anodes at 4-8 O’Clock position in the interval of 2 metre (max.) on carrier pipes at all cased crossings i.e. railways/ roads etc. | Item189 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
190 | Monitoring of the protection system for 6 months. | Item190
191 | All civil/ structural works related to TCP system including supply of bricks, cement & steel etc. required for completion of the system. | Item191 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
192 | For 12" | Item192 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
193 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item193 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
194 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item194 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
195 | FIELD INSTRUMENTATION | Item195 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
196 | PRESSURE INSTRUMENTS | Item196
197 | Supply , Installation of Pressure Gagues and their accessories inclusive of supply of necessary piping materials and tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/ manifolds & hydraulic testing (exclusive of calibration of instruments) as per installation standard attached elsewhere in Tender Document and Supply as per Data Sheet No.MEC/23K8/05/E5/I/001/DS-PG. Give breakup of supply and Installation rate. | Item197 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
198 | CALIBRATION | Item198
199 | Calibration of the instruments listed below including removal of instruments from pre-installed locations like panels, enclosure racks, fields etc. and refixing them back in respective/ required places, providing equipments, necessary test jigs, instrument air and all consumables. Calibration reports shall be prepared and to be submitted to the Purchaser/ Consultant. | Item199
200 | Pressure Gauges | Item200 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
201 | Note: | Item201 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
202 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item202 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
203 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item203 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
204 | PIPING WORKS FOR SECTIONALISING VALVE STATION-CUM-TAP-OFF POINT All works for fabriaction and installation of all piping above ground at all elevations and below ground at all depth for Sectionalising Valve Station alongwith preparation of construction drawings duly approved by EIC, in all type of terrains and soils including transportation and handling of all Owner supplied materials i.e. extended stem butt welded sectionalising gas actuated ball valve, other types of valves, line pipes for mainline, 4" NB pipe for all branch line including ventlines from Owner's designated place(s) of issue to work site. | Item204 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
205 | Contractor shall supply all required size & type of piping material like pipes, fittings & flanges etc. as per PMS alongwith 2" NB pipe for all branch line & vent line (wherever required) including supply of all consumables, manpower, machinaries, materials etc. and carrying out all mechanical works of underground and above ground piping including fabrication, welding, nondestructive testing of welds, weld repairs/ retesting, cleaning/ flushing, pre-hydrotesting & hydrostatic testing, dewatering, functional testing, cutting of mainline and bevelling (if required) | Item205
206 | assembly, including radiography of tie-in joints, corrosion, coating and external painting as required, installation of instruments like pressure/ temperature instruments/ gauges alongwith complete SS Tubing works including supply of SS Tube and thier accessories etc., as required, obtaining all statutory clearances, approvals and permissions for the works (wherever required), making of valve pit (for detail refer relevant drawings) for SV Stationscum- tap-off points enclosed with tender filled with sand, excavation and filling in all types of soils including soft/ hard rock for installation of piping/ pipe supports providing pipe supports, area fencing and gate including all associated civil and structural works; painting, finishing, clean-up and restoration of site; preparation of as-built drawings, documents and project records and performing all works as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge. In this item, instead of Brick Work RCC will be done | Item206 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
207 | Type - I SV Station on 12" Pipeline | Item207 | 1 | Lumpsum for each |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
208 | Note: i) Work under above items are exclusive of all works associated with main pipeline covered under Item No. 1.0 above. ii) All civil/ structural works including area fencing and gate, valve pits except for piping support will be paid separately as per unit rate provided elsewhere in the SOR. iii) All coupling, nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under above item rate. | Item208 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
209 | Details of Major Road Crossing (Canal/SH/DR/NHAI): Supply, Installation & Insertion of pipeline across Canal / State Highways as per SCC and technical specifications | Item209 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
210 | Supply & Installation of 24" NB x 6.4mm Wall thk. Casing pipe for Line Pipe 12"NB(6.4 mm thk API 5L Gr X52) by Jacking Boring . Including Insertion of 12" dia Carrier pipeline in 24" dia casing pipe and connectivity with existing pipeline at both end of National Highways/State Highways/ Railway as per SCC and technical specifications -Supply of Casing Pipe Supply of following casing pipe including handling, loading, transportation & unloading etc. to contractor's own stock yard / worksite(s). -After Completion of insertion of carrier pipe with Connectivity at both end including all works as per the scope of work -Post Hydro testing & Commissioning , Submission of as-built drawing, Submission of Documents - The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. | Item210 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
211 | Note: (i) Crossing width may vary as per site condition. Tenderer are advised to visit site for actual assessment of extent of crossing. Actual length of Boring shall be as per design calculations so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. (ii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by Boring method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item211 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
212 | (iii) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossings at different locations. | Item212 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
213 | (iv) Actual length & cover from top of casing pipe string may vary depending upon site conditions, approved drawings, specification etc. and / or as decided by concerned Authority / Engineer-in-charge. (vi) No Extra Payment for supply & installation of Zinc ribbon to be provided to Carrier pipe & Zinc Anode is to be provided to Casing pipe and its design included in above item | Item213 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
214 | Supply and installation of 24'' casing pipe,Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insertion of carrier pipe in casing pipe after above ground pretesting at specified test pressure and installation of casing insulators & Zinc ribbon anode as per specification/ drawings. Installation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed (Any type of soil) | Item214 | 80 | Mtrs |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
Total in Figures | [51 empty] | 0 | 0 | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## BoQ12 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR | [49 empty] | 1
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Maharastra Natural Gas Ltd.,Pune
Name of Work: TENDER FOR LAYING & CONSTRUCTION OF 12” NB X 6 KM U/G STEEL PIPELINE NETWORK & ASSOCIATED WORKS FROM NEAR NYARA PUMP, DHOKSAL TO HOTEL YUVRAJ, JATKHEDA ON NH548C (Section No-12)
Tender No: MNGL/CP/2024-25/109
Do you want to quote for this sheet ? |  |  | Yes
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE / SCHEDULE OF RATES (SOR) (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Rate inclusive of all taxes and duties except Goods & Service Tax (Rs.) | Per Unit Goods & Service Tax (GST) In % (To be entered by the Bidder) | GST in Rs. | Unit rate inclusive of all taxes & duties including GST (Rs.) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | CARBON STEEL PIPES | Item1
2 | PIPELINE LAYING / INSTALLATION in all type of surface (Normal/built-up surface) "Receiving and taking over" as defined in the specifications, handing, loading, transportation and unloading of Owner supplied 3-Layer PE coated linepipes from Owner's designated stack-yard to Contractor's stock yard/workshop/work-site including preliminary activities, preparation of drawings, wherever required for crossing etc. including handling, stacking, stringing on the pipeline Right-of-Use/ pipeline route alignment, carrying out inspection of company supplied materials including linepipes at the time of taking over, laying/ installation of coated linepipes, associated burried valves, barred tees, insulating joints, flanges & fittings of all sizes, thickness & ANSI class rating and accessories as per specification wherever required depending on site condition including execution of all works, "taking over", handling , including loading and unloading, transportation of Owner supplied materials other than linepipe from Owner's designated place (s) of issue to work site, | Item2 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3 | additional lands required for Contractor's storage, fabrication, access for construction, procurement and supply of all materials (except Owner supplied materials), consumables, equipment, labour and other inputs, carrying out all temporary, ancillary, auxiliary works, aquistion of ROU/ROW for laying of pipeline from HDD Exit and entry point to Tie in Point of existing Pipeline/ ROU, ready for commissioning of pipeline as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge, including but not limited to carrying out the following works: | Item3 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4 | Surveying of route and detours required at the time of execution including marking the same in topographical sheet, preparation of construction drawings showing survey details, and submit same to Owner for review / approval. | Item4
5 | Staking and installation of construction markers, clearing, fencing, grubbing, cutting of trees, full filling all the requirements of various statutory/ environment authorities to the entire satisfaction of concerned authorities, grading of work area. Shifting of all obstruction within the ROU/ Pipeline route alignment viz. electrical lines/ poles, telephone line / poles, etc. coordination with concerned authorities and obtain permissions from these authorities. | Item5
6 | Trenching to all depths by excavation in all types of soils including soft/ hard rock and different type of pavement / footpath / roads etc. including rock breaking, chiselling or otherwise cutting etc. as required and storing excavated soil, reusable materials at designated area as directed by Engineer in charge and to a width to accommodate the Steel pipeline as per the relevant standard/ specification etc. [The minimum depth of the top of pipeline shall be 1.2m measured from top of pipeline coating to the top of undisturbed surface of the soil or as per SCC/ OISD - 141 / 226, whichever is higher]. Dewater of trenches if required as per site condition. | Item6
7 | Carrying out repairs of pipe defects/ replacement in case of irreparable defects and repairs of defects of pipe coating not attributable to Owner including defects/ damages occurring during transportation / handling. | Item7
8 | Stringing of line pipes along pipeline trench / ROU on straw / sand / soft soil bags including supply of bags and its filling materials. | Item8
9 | Checking, cleaning, aligning, bending, cutting and bevelling (as required) of pipes for welding and field adjustments including pipe fittings, welding, carrying out non-destructive testing of welds as required including 100% radiography by X-ray and providing all requisite equipment, labour, supervision, materials, films, consumables, all facilities and personnel to process, develop, examine and interpret radiographs and other tests as required, carrying out repairs of weld joints found defective by Engineer-in-Charge, carrying out re-radiography and other tests as required on repaired joints. | Item9
10 | Carrying out installation of carrier line pipe at all minor crossing viz. carttrack, pathway, water bodies etc. at designated depth by open cut (except at crossing by HDD method). | Item10
11 | Carrying out installation of carrier line pipe in the casing pipe at cased crossing (excluding installation of casing pipes which is covered separately). | Item11
12 | Coating of field weld joints, long radius bends (R=3D), elbows, buried fittings and valves etc. including supply of coating materials etc. (i.e. heat shrinkable sleeves and high build epoxy etc.) as per PJS & Technical Specification compatible with 3 layer PE coating material of the line pipe. | Item12 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
13 | Counting the number and type of trees cut in presence of DFO/concerned authorities and keeping record thereof, stacking and handing over of all cut tress. | Item13
14 | Installation / lowering the pipeline in trench to required depth as per PJS, Techanical Specification & drawings, supply & placement of 1.0mm thk. HDPE Yellow colour warning mat,RCC tiles (300 mm width x 50 mm thick) over the pipeline in same trench along the complete route as per standard drawings, data sheets & technical specifications, padding around pipeline as per Standard Drg. no. MNGL/Plng./Steel/03 with suitable soil duly approved by EIC including supply of padding material, backfilling and its compaction to the satisfaction of concerned authorities with excavated earth / borrowed select soil including supply of borrowed select soil duly approved by EIC before backfilling and make ready for restoration to be done by Onwer / concerned authorities. | Item14
15 | Supply and installation of slope breakers, wherever required or, as directed by Onwer / Engineer–in–charge. | Item15
16 | Crossing the all-foreign pipeline / HT line / cable / any other utilities etc. with necessary concrete / HDPE sheet protection including coordination with all agencies and obtaining NOC | Item16
17 | Supply and installation of bank protection alongwith backfill materials duly approved by EIC for pipeline trench and banks falls under minor water body crossing as per technical specification & Std. Drg. No. MNGL/Plng./Steel/28, wherever required or, as directed by Onwer / EIC. | Item17
18 | Training and diversions of streams in steep slope area, wherever required. | Item18
19 | Carrying out air cleaning, pigging, flushing, cleaning and hydrostatic testing of complete pipeline with required quantity of corrosion inhibitor including pre-testing of designated sections complete as per specification and approved by Engineer–in–charge to specified pressures indicated elsewhere and duration after stabilization as per specification, providing all equipment, pumps, fittings, instruments, dead weight tester, pressure recorder, thermocouples etc., and services, supervision, labour, consumables, water including supply of corrosion inhibitor, air, etc. as required, locating of leaks and rectification of defect attributable to Contractor (rectification of defects in linepipe material not attributable to contractor shall be paid separately as per other item of schedule of rate), re-testing after rectification, dewatering after successful completion of hydrotesting of entire section and as per specification | Item19
20 | All tieing-in, including the tie-in(s) of the pipeline with the adjacent sections of pipeline including cutting of test header, rebevelling as required, radiography and other NDT examination, joint coating as per specification. | Item20
21 | Final clean-up of right-of-use or area disturbed by contractor during their construction activities for laying of pipeline works and disposal of debris and surplus material to designated disposal areas and backfilling of trench and compaction of the same as per satisfaction of Owner and / Or as directed by Engineer–in–charge. | Item21
22 | Installation of all burried valves (except extended stem valves) inside the valve pit and making provision to operate the valve. | Item22 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
23 | Preparation of as-built drawings, pipe-books (1 set of tracing on polyester film and 6 sets of as-built drawings and 1 soft copy and 6 hard copies of pipe book) All the works shall be executed in accordance with the provision of contract including carrying out all temporary/ ancillary/ auxiliary works required for the performance of the works and all other acts, deeds, matters and things necessary to make the pipeline ready for precommissioning activities. | Item23 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
24 | Raking up of hard surface of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. Payment for cutting of hard rock, if any, is covered unders SOR no. 76 | Item24 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
25 | Specified dia Thk (mm) Material Coating Type Length of each pipe (mm) NB | Item25 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
26 | 305 (approx.) 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item26 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
27 | Note: This item shall be applicable for the underground steel grid main pipeline & branch pipeline, barred tees, insulating joints, bends, flanges & fittings, accessories etc. (i.e. including arrangement for making provision for tap-off on proposed steel grid main pipeline) and aboveground approach pipeline upto Insulating Joint (excluding installation of aboveground insulating joint) for various stations. | Item27
28 | Items except above are covered separately. The lengths of pipelines are tentative. | Item28 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
29 | Permission Liasioning /Follow-up | Item29 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
30 | Liasioning & follow up for Permission with all the concerned authorities & boards viz Railways, NH, PWD, MIDC, Local Municipal, Panchyat, Electricity, REC, RES, Sewage water, Drinking water, Forest, Social Forestry, Owners of OFC, Traffic, Law & Order, Fire Brigade, Private Land Owner etc. for entire pipeline length and associated terminals (like SVs, tap-offs) alongwith associated work as per tender. | Item30 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
31 | Laying of RCC Tiles | Item31 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
32 | Providing single layer of RCC Tiles with supply of RCC Tiles to entire width of trench above Warning Mat placed in trench over the laid pipeline as per standard drawing, specification and instruction of Owner. (Rate to include cost of all labour, tools, tackles, equipment, hire charges & supply of all materials, etc.) | Item32
33 | For width of 12" pipeline trench | Item33 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
34 | Barricading to comply with HSSE | Item34 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
35 | Steel barricading of the trenches Cautionary Sign Boards and lighting arrangement shall be provided as per attched drawing no.MNGL/Plng./steel/04. The rates include barricading of trenches along with sign boards, lighting etc. and maintain the same till the back filling of the trench. Rates will be payable per metre of BARRICADING PROVIDED. If proper barricading is not provided, MNGL will barricade the trenches at the risks and costs of the CONTRACTOR and will levy penalty of twice the rate per unit for the relevant section of the pipeline apart from other actions as per contract. | Item35 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
36 | RESTORATION OF ROADS Restoration of asphalt / concrete / red stone roads / pavement/Footpath/Paver block including compaction of soil, to original condition as per requirement and to the entire satisfaction of EIC and / or concerned Owners having jurisdiction for following thickness. | Item36 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
37 | Restoration of Asphalt road upto 10 cm thickness | Item37 | 800 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
38 | Restoration of Asphalt road beyond 10 cm upto 20 cm thickness | Item38 | 200 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
39 | Restoration of Concrete road upto 10 cm thickness | Item39 | 800 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
40 | Restoration of red stone road / footpath / pavement/ Paverblock upto 4 cm thickness | Item40 | 900 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
41 | BORROWED SELECT SOIL FOR BACKFILLING Additional work over and above item 1.0 for supply of specified and approved quality of borrowed soft graded soil / sand in place of available excavated material and / or other suitable soil as per applicable standards / specifications, including backfilling of excavated trench for specified length after laying and padding of pipeline, including transportation of such special backfill material over all distances, complete. | Item41 | 900 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
42 | CROSSING OF STEEL PIPELINE BY OPEN CUT | Item42
43 | Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insatllation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed. | Item43
44 | Road Crossing By Open Cut Method Road Crossings at various locations by Open cut Method as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item44 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
45 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method | Item45 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
46 | Water body Crossing By Open Cut Method water/ canal/ nallah/ drain/ channel Crossings at various locations by Open cut Method as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item46 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
47 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method | Item47 | 90 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
48 | Note: Laying of the pipeline by the approved method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item48
49 | Backfilling of the Road/water/ canal/ nallah/ drain/ channel Crossings/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority. | Item49
50 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item50 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
51 | CROSSINGS/LAYING ALONG THE ROAD BY HDD METHOD | Item51
52 | Complete work of the any crossing (between the limits are defined as approved drawings) by HDD method including "Receiving and taking over" owner supplied three layer PE coated line pipes from Owner's designated place to issue/ dump site(s) and transportation to Contractor's stock yard/ work shop/ work site including all handling loading, unloading, aligning etc. supply of all Contractor supplied material, manpower, equipment, other resources and aquiring the required land for storage, fabrication inclduing string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type Heat Shrink Sleeve and repair of pipeline coating with special repair patch materials as per specification,pre-testing etc. of complete string made for crossing access for Contractor etc and execution of, but not limited to, following works in accordance with specifications scope of work and instructions of Engineer-in-charge and as per all provision of Contract Document. | Item52
53 | Pre-construction surveys based on site visit, collection of historical data from irrigation/ concerned department including design & calculation and detail engineering and making of crossing drawing for getting their approval from concerned Authority/ Engineer-in-charge, getting work permit/ NOC for water crossings/ road crossings as well as utility crossings (if any) encountered during crossing prior to start the execution of work. | Item53 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
54 | Directional drilling to required depth from top of road including maintenance of drill hole in all types of strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) at all depth to accommodate the pipeline at all conditions encountered during rail/ road crossing by approved HDD methods for providing minimum cover specified in code/ specification or the actual depth as decided by concerned authority, whichever is more. | Item54 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
55 | In case of water crossing, drilling to the required depth on the banks and bed including maintenance of drill hole in all types of soil strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) all depth to accommodate the pipeline a by HDD methods for providing with minimum cover over top of the pipe at all point across the maximum possible width of water bed (as per drawing) either 1.5 mtrs. below the predicted scour profile expected during the life time of the pipeline or 2.5 mtrs. below the available lowest firm bed (if scour profile/ depth not available) of the water crossing by ascertaining bed level upto 50 mtrs. both the side from crossing location or the actual depth as decided by concerned Authority/ Engineer-in-charge whichever is more. | Item55 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
56 | Laying of the pipeline by the approved HDD method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints with special type Dirax Heat Shrink Sleeve or equivalent and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item56 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
57 | Backfilling of the ditch/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority and all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specification, approved drawings, calculations, methods and to the satisfaction of Engineer-in-charge and/or as directed by concerned Authority. | Item57 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
58 | Post installation hydrotest dewatering and tie-in with pipeline at either side of crossing/banks etc. | Item58 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
59 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item59 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
60 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 by HDD Method . | Item60 | 120 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
61 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item61 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
62 | Installation of carrier pipes by rock drilling for Road/water/Canal/ nallah/ drain/ channel/along the road, or wherever required in all types of hard rock. It includes survey of the underground utilities, submission of profile for approval, execution of the work as per the standard procedure, including , excavation of the pits, insertion/pulling of the carrier pipe, removal of malba, subsequent backfilling and restoration of the facility crossed as per original condition, including supply of all other materials, equipment, consumables, manpower etc including string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type of Heat Shrink Sleeve (Direx) and repair of pipeline coating with special repair patch materials as per Specification, pre-testing etc. of complete string made for crossing/ laying access for Contractor etc. and execution of, but not limited to, following works in accordance with specifications and instruction of Engineer-in-Charge and as per all provision of Contract Document. Balance activities as defined in SOR Item of open trench. Note:The length of HDD mentioned is tentative and may vary to the considerable extent depending upon requirements as per site conditions. The length mentioned in SOR is indicative for all the crossing to be done by HDD, numbers and locations shall be decided by Engineer-in-Charge depending upon site condition. Payment for the length of final tie-in carrier pipeline string with mainline laid by HDD are inclusive in this above item rate. No separate payment shall be made under other clauses mentioned elsewhere. Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item62
63 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 by HDD Method . | Item63 | 110 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
64 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item64 | 90 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
65 | Note: (i) Crossing width & Actual string length for HDD shall vary as per design calculations & site condition so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. | Item65
66 | (ii)Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item66
67 | (iii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by HDD method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item67
68 | (iv) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossing at different locations. | Item68
69 | (v) The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. | Item69
70 | Note: (i) Quantity mentioned under item nos. 44, 46 are indicative only for different location of roads/water/ canal/ nallah/ drain/ channel Crossings. (ii) Actual length & width of individual crossing and cover from top of casing pipe/ carrier pipe string may vary depending upon site condition, approved crossing drawings, specifications etc. and / or as decided by Engineer-in-charge/ Concerned Authority. | Item70
71 | (iii) Payment for supply & installation of Zinc ribbon anode and its design excluded from above item and covered elsewhere in the SOR. (iv) Payment for the length carrier pipeline string inserted in casing pipe laid by Boring are covered separately and shall be paid under other clauses mentioned elesewhere in the SOR. | Item71
72 | Excavation beyond 1.5m depth in case of crossing of utilities/ drain/ culverts etc. through open cut upto the following depth (including restoration of the damaged area to its original condition and satisfaction of the Engineer-in-charge / concerned authorities) : - | Item72 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
73 | In all type of surface (Kachha/ built-up surface / Hard surface) of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. The other activities are as per SOR 1.1. Payment for cutting of hard rock, if any, is covered unders SOR no. 76 | Item73
74 | Deeper than 1.5 m & upto 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item74 | 700 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
75 | Deeper than 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item75 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
76 | Excavation of hard rock | Item76
77 | Excavation of hard rock wherever hard rock of single piece exceeding 1.0 m in length removable by pneumatic chisel/ drill as per direction of EIC. | Item77 | 3800 | Cub. M |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
78 | REPAIR OF COATING DEFECTS (NOT ATTRIBUTED TO CONTRACTOR) | Item78
79 | Repair of Holiday in Coating (Noted and recorded at the time of "receiving and taking over") Supply of all coating repair materials as per requirements of specification to be compatible with line pipe coating material, supply of all consumables, utilities, equipments and all manpower required, pipe cleaning and surface preparation, repairing of coating defects (resulting in holiday) and testing including all handling, transportation, etc. for line pipes, performing all works necessary for the completion of the works stirctly in accordance with relevant specification and instructions of Engineer-In-Charge. This rate shall be applicable per sq. cm of the exposed steel area exposed steel area. | Item79 | 2200 | Sq. cm. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
80 | PERMANENT MARKERS Supply, fabrication and installation of all types of permanent markers along the route including all associated civil works such as excavation in all types of soil, construction in all types of soil, construction of pedestals and grouting with concrete, clearing, supply and application of approved colour and quality of primer and paint, stencil letter cutting for numbers, direction, change etc., restoration of area to original condition and performing all works as per drawing, specification and instruction of engineer-in-charge. | Item80
81 | Pipeline RCC boundary / route marker as per drawing | Item81 | 120 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
82 | Pipeline warning markers with post & foundations | Item82 | 40 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
83 | Pipeline direction marker with post & foundations | Item83 | 25 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
84 | Pipeline KM with post & foundations | Item84 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
85 | HOOK -UP | Item85
86 | Hook-up of proposed pipeline by welding of final tie-in-joint with any existing laid pipeline portion of river X-ing ,existing Tap-off & battery limit of section IV including Hook-up point of the existing pipeline to be made ready for welding by cutting of flanges / valves / headers at all depth in all type of soil etc. Venting of N2 / gas / gas mixture as required purging of N2 Gas (if required), rebevelling as required, radiography and other NDT examination, joint coating as per specification.Contractor shall supply of all consumables, manpower, machinaries, materials, N2 gas etc. and carry out all works as per the provisions of Contract document and instructions of Engineer-in-charge. | Item86
87 | For 12" NB | Item87 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
88 | PRE-COMMISSIONING AND ASSISTANCE IN COMMISSIONING OF PIPELINE SYSTEM Swabbing, drying, purging with nitrogen of the complete pipeline network and the associated facilities being installed to the specified acceptance criteria, carrying out pre-commissioning works, providing assistance during the complete duration of commissioning operations for entire pipeline network system including supply of all equipment, man-power, consumables (including pigs & nitrogen required for purging with maintaining nitrogen column of mininum 10% of pipeline geometric volume) materials for all temporary works and performing all associated works, complete as per the relevant specifications, other provisions of Contract document and instructions of Engineer-in-charge. | Item88
89 | For 12" NB Pipeline | Item89 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
90 | IDLE TIME PRESERVATION OF PIPELINE Preservation of complete pipeline and associated facilities forming part of the pipeline as per Bid document and its maintenance including supply of all consumables, all equipment, manpower, etc. complete as per the requirements of specifications, other provisions of Contract document and instructions of Engineer-in-charge. Note : Owner reserves the right to exercise either or none of the rates below. | Item90
91 | By filling and pressurizing with nitrogen to a pressure of 2 bar(g) for a period of 3 months. | Item91 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
92 | For 12" NB Pipeline | Item92 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
93 | For every additional period of one month or part thereof | Item93 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
94 | For 12" NB Pipeline | Item94 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
95 | RCC VALVE PITS All civil works including supply of all materials, excavation of pit, piping supports including all PCC and RCC works for valves pits including pedestals with insert plates as required sealing of pipe at valve pits, providing cover etc. and finishing , clean-up and restoration of site, filling and grading of area around valve station for avoiding any local flooding of area, as per typical drawing and specification enclosed and instructions of Engineer-in-charge. In this item, instead of Brick Work, RCC will be done | Item95 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
96 | Valve Pit of Size 2m x 2m | Item96 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
97 | SUPPLY OF ASSORTED PIPE, FITTINGS AND FLANGES Complete works of supply of pipes, flanges & fittings for aboveground & underground installation including all taxes, duties, transportation and inspection charges but not limited to, the following items in accordance with PMS (piping material specification), relevant specifications & drawings indicated in job specification under SCC (technical) and instructions of Engineer-in-charge and as per all provisions of the CONTRACT DOCUMENT. - Handling including lifting, transportation from Contractor Stores to CONTRACTOR's workshop for fabrication and/ or to work site for field fabrication and erection for all piping items supplied by Contractor. | Item97
98 | Carbon Steel Pipe (A 106, Seamless B-36.10/ API X 52 ) | Item98
99 | Size Rating/ Schedule | Item99 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
100 | 2" NB, BE Sch. 80 | Item100 | 56 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
101 | 1" NB, PE Sch. 80 | Item101 | 38 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
102 | ¾" NB, PE Sch. 160 | Item102 | 36 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
103 | Flanges | Item103
104 | Weld Neck (B-16.5, 300# A105,125 AARH, Serrated finish) | Item104
105 | Size Rating/ Schedule | Item105 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
106 | 2" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item106 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
107 | Blind Flanges (B-16.5, 300# A105,125 AARH Serrated) | Item107
108 | Size | Item108
109 | 2" NB, RF | Item109 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
110 | Elbow (Seamless) | Item110 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
111 | 90° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item111
112 | Size Rating/ Schedule | Item112
113 | 12" NB 300# | Item113 | 24 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
114 | 45° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item114 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
115 | Size Rating/ Schedule | Item115
116 | 12" NB 300# | Item116 | 24 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
117 | 90° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item117 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
118 | Size Rating/ Schedule | Item118
119 | 12" NB 300# | Item119 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
120 | 45° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item120
121 | Size Rating/ Schedule | Item121
122 | 12" NB 300# | Item122 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
123 | 22½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D) Min Thickness 6.4mm | Item123 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
124 | Size Rating/ Schedule | Item124
125 | 12" NB Sch. Std. | Item125 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
126 | 11½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D), Min Thickness 6.4mm | Item126
127 | Size Rating/ Schedule | Item127
128 | 12" NB 300# | Item128 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
129 | Tees (Seamless) | Item129
130 | Equal Tee (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item130
131 | Size Rating/ Schedule | Item131
132 | 12" NB x 12" NB x 12" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item132 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
133 | 2" NB x 2" NB x 2" NB Sch. XS | Item133 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
134 | Weldolet and Sockolet | Item134
135 | Weldolet (MOC A105 & DIM. MSS SP 97) | Item135
136 | Size Rating/ Schedule | Item136
137 | 12" NB x 2" NB Sch. 80. | Item137 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
138 | Sockolet (MOC A105 & DIM. MSS SP 97) | Item138
139 | 12" NB x 3/4" NB #6000 | Item139 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
140 | Butt Weld Disc End Cap (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item140
141 | Size Rating/ Schedule | Item141
142 | 12" Sch. Std. | Item142 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
143 | Fabrication & Installation of Underground Valve Assembly | Item143 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
144 | 12"NB Isolation Valve/tap-off assembly as per Drg. No. MNGL/Plng./Steel/40 | Item144 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
145 | Note: | Item145 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
146 | For all the supply items mentioned above, procurement shall be made as per enclosed Data Sheets and respective technical specification, after due approval of Engineer-in-charge. | Item146
147 | The quantities mentioned above are tentative and quantities for above supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item147
148 | PLANT PIPING (ABOVEGROUND) Fabrication and testing of carbon steel piping and fittings, valves, IJ, including supply of all consumables, equipment, manpower, and other resources and execution of job as per instruction AIC/EIC.Transportation of all piping items from Owner's and/ or Contractor's storage point to work at site/ workshop as applicable, complete work of fabrication, erection, painting, testing of pipes, flanges and fittings and making ready for further Commissioning / Start-up of carbon steel piping of all sizes and ratings including supply of all consumables, equipment, manpower and other resources and execution of, but not limited to, as per all provisions of the CONTRACT DOCUMENT. | Item148 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
149 | Fabrication including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site, cutting, edge preparation, inclusive of grinding the edges of pipes, fittings, flanges, reducers etc. to match with the matching edges of uneven thickness, wherever required, fit-up, welding of pipes and fittings like elbows, tees, reducers, weldolets, sockolets, Valves, IJ etc. flanges, vent and drain point connection, Radiography and NDT of all joints etc, including providing stubin connections, fabricated fittings and reinforcement pads etc., as required. | Item149 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
150 | Erection of pipes of all types and thickness at all elevations, connecting with equipment nozzle, aligning, installation and carrying out connected activities for all types of valves, all online instruments and fittings of all sizes of elbow, reducers, tees, flanges, blind flanges, spectacle blind flanges, branch connection / tapping for pressure gauges, including installation of gaskets and bolts. | Item150 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
151 | Erection including prior cleaning, lifting, placing on pipe sleepers and supports, overhead on racks, skids and at all elevations including installation and carrying out connected activities for all types of valves including supply and fixing of gaskets, studs/ bolts, nuts wherever required for all sizes, levelling, aligning, joining of flanges, blind flanges, connecting with equipment, nozzles, strainers, tie-in with existing piping/facilities, etc. tapping for inline instruments like pressure gauges, thermowells, sample connection, etc. | Item151
152 | Hydro testing of the piping job shall be conducted at pressure mentioned in specification for a period of 4 hours by using de-mineralised water, to check its strength. No visible leakages shall be detected during the test. Testing shall be conducted as per tender specification. | Item152
153 | Preparation of final bill of material based on piping GADs. | Item153
154 | Preparation of isometric and fabrication drawings. | Item154
155 | Carrying out Non-destructive testing as required | Item155
156 | Painting of entire system (including aboveground all pipes fittings, flanges and accessories) as per specifications suitable for highly corrosive area environment including supply of approved paints and primers, application of primer and paints, indentification lettering/ numbering, colour coding, etc. as specified including rub down & touch up of shop primer or scrapping of shop primer wherever required by COMPANY and providing scaffolding for all heights etc. | Item156
157 | Cleaning and flushing by water/ compressed air, testing of the systems including hydrostatic, pneumatic and any other type of testing as specified, draining, drying by compressed air/other methods approved by COMPANY. | Item157
158 | Precommissioning & making operational all piping system and equipments. | Item158 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
159 | Commissioning Contractor scope shall provide all necessary assistance in term of supply of man-power, equipment, tools and tackles required amount of nitrogen for purging of entire terminal piping system including equipments etc. to the company during commissioning activities. | Item159 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
160 | Completion of all such work in all respects as per scope of work and as per drawings, specifications and instructions of the COMPANY and keeping the system ready in all respects for further commissioning and start up. | Item160 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
161 | Hook-up works (with client/ consumer piping at battery limits): | Item161 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
162 | Complete Carbon Steel aboveground Piping Work with painting including all fittings, flanges and supply of all required gaskets, studs bolts & nuts etc. and Any other work and material required for the completion of the work and not covered above and desired by EIC shall be in the scope of contractor | Item162 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
163 | Carbon Steel Pipe (ASTM A 106, Seamless B-36.10 / API X 52) | Item163 | 150 | inch Dia |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
164 | 1) Pipe Specification and thickness may vary depending upon availability of pipe. No extra payment shall be made for this. 2) All butt welded fittings & flanges end shall generally match with connecting pipe wall thickness. However, in case of misalignment, Contractor shall have to do end preparation without any extra cost. 3) All o-lets less than 2" NB size, all sizes of coupling and nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under erection rate. | Item164 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
165 | Aboveground installation of Insulating Joint & Valves etc. Handling including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site and installation of all types of valves, insulating joint including assembly of valve accessories, (if any) by bolting, threading or welding, supply and insertion of gaskets, nuts & bolts, nipples, etc. at all elevations of pipe sleepers, supports or overhead on racks, equipments nozzle, skid & painting etc. supply of all consumables, manpower, equipment, etc. for completion of all works as per scope of work and as per drawings, specifications and instructions of Engineer-in-charge including servicing/ cleaning of valve wherever requried. | Item165 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
166 | 12" NB, 300# - Insulating Joints | Item166 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
167 | STRUCTURAL WORKS | Item167 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
168 | Supply of erection of single leaf mild steel gate 2.5m high with mesh upto 2m height and barbed wire fencing and 2m wide complete in all respect including painting as per TS on all MS items, all works as per specification and drawings excluding foundations and RCC beams. | Item168 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
169 | Supply of all materials, fabrication and erection of chain link fencing 2.5m high with mesh up to 2m height and barbed wire fenching complete in all respects including painting as per TS on all MS items, all works as per specification and drawings excluding foundation and RCC beams. | Item169 | 200 | RM |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
170 | Pipe Supports & Other Structures | Item170 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
171 | Supply, fabrication and erection of all types of pipe supports like clamps, saddle, guide stops, cradles, turn buckles, anchors, T-posts; stockade/ trestle and pipe bridge for overhead piping; frames for canopy, approach ladders and platforms, crossover, cable tray supports, etc. including painting suitable for highly corrosive area as per specification labour and supervision & complete work as per drawings, specifications and instruction of Engineerqw-incharge. (Bolts, nuts, washers, U-clamps etc. for supporting shall be supplied by the Contractor within the rates quoted. These items will not be measured and paid seperately). The work is to be completed in all respect as per scope of work and specification. | Item171 | 250 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
172 | Notes: | Item172 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
173 | The quantities indicated are estimated values and hence are approximate. Final payment will be made based on actual quantities to be certified by the Purchaser. | Item173
174 | The cost of MS bolts (permanent and service(, washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants etc., as required for the work shall be deemed to be included in the quoted rates. | Item174 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
175 | All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accrodance with time schedule, are deemed be included in the quoted rates. | Item175
176 | CIVIL WORKS | Item176
177 | Site Grading Excavation in earth and filling to the grades and levels shown in the approved drawings in all kinds of conditions including for Road embarkments, using approved quality good earth from designated borrow area, for all heights and depths including clearing and stripping (min. 150mm) of the area marked for filling, taking spot levels, consolidating the exposed natural soil surface, excavating the earth from borrow area loading, transporting & unloading, spreading in layers not exceeding 150mm thickness, breaking clods, watering (if reqd.), ramming and compacting by manual/ mechanical means to give minimum 92% of modified Proctor's density of earth, testing & dressing including disposal of all unserviceable material all complete as per specifications and directions of Engineer-in-charge. | Item177 | 200 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
178 | (Rate to include cost of all labour, tools, tackles, equipment, hire charges, cost of borrow earth by way of royalties, right of way, cess etc., as applicable with all bye works and sundry works). | Item178
179 | Plain Cement Concrete Supplying and laying plain cement concrete (including shuttering of required) in all types of concrete works including levelling courses below foundation, substructure, superstrcuture, chambers, cable tranch, under floors and any other locations, at all leveies as per drawings, specifications and directions of the Engineer-in-charge. | Item179
180 | PCC 1:2:4 1 Cement : 2 Coarse sand : 4 stone aggregate 20mm nominal size. | Item180 | 500 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
181 | Reinforced Cement Concrete Providing and laying reinforced cement of grade M-20 with 20mm and down grade crushed stone aggregate in all types of structures like foundations, pedestals, pedestal bases, pipe supports, sleepers cable trench inlcuding constrcution joints, bitumen painting on surface in contact with soil, providing and fixing reinforcing steel, shuttering, inserts, finishes etc. at all depths and heights complete as per drawings, specifications and direction of the Engineer-incharge. | Item181 | 400 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
182 | Rate to include cost of all labour, tools, tackles, equipment, hire charges, supply of all maerials such as minimum 43 grade cement including sulphate resistant cement for substructures, R/F steel, Inserts, bolts, conduits, bitumen, other minor constrcution materials, shuttering, stanging, earthwork in excavation and backfilling using serviceable earth in all conditions, shorting bailing and pumping out water, testing of concrete, curing etc. with all bye works and syndry works. | Item182
183 | TEMPORARY CATHODIC PROTECTION SYSTEM | Item183
184 | Design, detailed engineering, supply, installation, testing and commissioning of the temporary Cathodic protection system using Mg/ Zn galvanic anodes to protect the external surface of 3 LPE coated entire 5.5 km (approx.) long steel pipeline network against corrosion for design life of minimum 1 year or till commissioning of PCP system whichever is later as per standard specification No. MNGL/Steel/TS/15 for temporary cathodic protection system. Scope shall also include but not limited to the following for completion of jobs: | Item184 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
185 | Measurement of soil resistivity along the right of way of the main pipeline route as per specification for design & installation of anodes. | Item185
186 | Collection of additional data related to cathodic protection along the right of way of pipeline as per specifications. | Item186 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
187 | Supply, installation, testing & commissioning of one set of spark gap arrestor with 2 plate Zinc grounding cell of 20 kg net weight each across each insulating joint as per specification. | Item187
188 | Supply, installation, testing & commissioning one set of polarisation cell with zinc anode at all high tension (66KV or higher) electrical power transmission line/Equipment crossing or running parallel to the pipeline for grounding purpose as per specification. The rating shall depend upon anticipated fault current & ground bed resistance at the location of installation. However, the rating of polarisation cell (krick) shall not be less than 5 KA & number of 20 kg net weight zinc anode shall not be less than two. | Item188
189 | Supply & installation of Zinc Ribbon Anodes at 4-8 O’Clock position in the interval of 2 metre (max.) on carrier pipes at all cased crossings i.e. railways/ roads etc. | Item189 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
190 | Monitoring of the protection system for 6 months. | Item190
191 | All civil/ structural works related to TCP system including supply of bricks, cement & steel etc. required for completion of the system. | Item191 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
192 | For 12" | Item192 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
193 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item193 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
194 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item194 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
195 | FIELD INSTRUMENTATION | Item195 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
196 | PRESSURE INSTRUMENTS | Item196
197 | Supply , Installation of Pressure Gagues and their accessories inclusive of supply of necessary piping materials and tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/ manifolds & hydraulic testing (exclusive of calibration of instruments) as per installation standard attached elsewhere in Tender Document and Supply as per Data Sheet No.MEC/23K8/05/E5/I/001/DS-PG. Give breakup of supply and Installation rate. | Item197 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
198 | CALIBRATION | Item198
199 | Calibration of the instruments listed below including removal of instruments from pre-installed locations like panels, enclosure racks, fields etc. and refixing them back in respective/ required places, providing equipments, necessary test jigs, instrument air and all consumables. Calibration reports shall be prepared and to be submitted to the Purchaser/ Consultant. | Item199
200 | Pressure Gauges | Item200 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
201 | Note: | Item201 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
202 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item202 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
203 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item203 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
204 | PIPING WORKS FOR SECTIONALISING VALVE STATION-CUM-TAP-OFF POINT All works for fabriaction and installation of all piping above ground at all elevations and below ground at all depth for Sectionalising Valve Station alongwith preparation of construction drawings duly approved by EIC, in all type of terrains and soils including transportation and handling of all Owner supplied materials i.e. extended stem butt welded sectionalising gas actuated ball valve, other types of valves, line pipes for mainline, 4" NB pipe for all branch line including ventlines from Owner's designated place(s) of issue to work site. | Item204 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
205 | Contractor shall supply all required size & type of piping material like pipes, fittings & flanges etc. as per PMS alongwith 2" NB pipe for all branch line & vent line (wherever required) including supply of all consumables, manpower, machinaries, materials etc. and carrying out all mechanical works of underground and above ground piping including fabrication, welding, nondestructive testing of welds, weld repairs/ retesting, cleaning/ flushing, pre-hydrotesting & hydrostatic testing, dewatering, functional testing, cutting of mainline and bevelling (if required) | Item205
206 | assembly, including radiography of tie-in joints, corrosion, coating and external painting as required, installation of instruments like pressure/ temperature instruments/ gauges alongwith complete SS Tubing works including supply of SS Tube and thier accessories etc., as required, obtaining all statutory clearances, approvals and permissions for the works (wherever required), making of valve pit (for detail refer relevant drawings) for SV Stationscum- tap-off points enclosed with tender filled with sand, excavation and filling in all types of soils including soft/ hard rock for installation of piping/ pipe supports providing pipe supports, area fencing and gate including all associated civil and structural works; painting, finishing, clean-up and restoration of site; preparation of as-built drawings, documents and project records and performing all works as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge. In this item, instead of Brick Work RCC will be done | Item206 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
207 | Type - I SV Station on 12" Pipeline | Item207 | 1 | Lumpsum for each |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
208 | Note: i) Work under above items are exclusive of all works associated with main pipeline covered under Item No. 1.0 above. ii) All civil/ structural works including area fencing and gate, valve pits except for piping support will be paid separately as per unit rate provided elsewhere in the SOR. iii) All coupling, nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under above item rate. | Item208 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
Total in Figures | [51 empty] | 0 | 0 | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## BoQ13 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR | [49 empty] | 1
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Maharastra Natural Gas Ltd.,Pune
Name of Work: LAYING & CONSTRUCTION OF 12” NB X 6 KM U/G STEEL PIPELINE NETWORK & ASSOCIATED WORKS FROM HOTEL YUVRAJ, JATKHEDA ON NH548C TO NEAR HOTEL TULJA BHAVANI, MANTHA ON NH 548C (Section No-13)
Tender No: MNGL/CP/2024-25/109
Do you want to quote for this sheet ? |  |  | Yes
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE / SCHEDULE OF RATES (SOR) (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Rate inclusive of all taxes and duties except Goods & Service Tax (Rs.) | Per Unit Goods & Service Tax (GST) In % (To be entered by the Bidder) | GST in Rs. | Unit rate inclusive of all taxes & duties including GST (Rs.) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | CARBON STEEL PIPES | Item1
2 | PIPELINE LAYING / INSTALLATION in all type of surface (Normal/built-up surface) "Receiving and taking over" as defined in the specifications, handing, loading, transportation and unloading of Owner supplied 3-Layer PE coated linepipes from Owner's designated stack-yard to Contractor's stock yard/workshop/work-site including preliminary activities, preparation of drawings, wherever required for crossing etc. including handling, stacking, stringing on the pipeline Right-of-Use/ pipeline route alignment, carrying out inspection of company supplied materials including linepipes at the time of taking over, laying/ installation of coated linepipes, associated burried valves, barred tees, insulating joints, flanges & fittings of all sizes, thickness & ANSI class rating and accessories as per specification wherever required depending on site condition including execution of all works, "taking over", handling , including loading and unloading, transportation of Owner supplied materials other than linepipe from Owner's designated place (s) of issue to work site, | Item2 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3 | additional lands required for Contractor's storage, fabrication, access for construction, procurement and supply of all materials (except Owner supplied materials), consumables, equipment, labour and other inputs, carrying out all temporary, ancillary, auxiliary works, aquistion of ROU/ROW for laying of pipeline from HDD Exit and entry point to Tie in Point of existing Pipeline/ ROU, ready for commissioning of pipeline as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge, including but not limited to carrying out the following works: | Item3 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4 | Surveying of route and detours required at the time of execution including marking the same in topographical sheet, preparation of construction drawings showing survey details, and submit same to Owner for review / approval. | Item4
5 | Staking and installation of construction markers, clearing, fencing, grubbing, cutting of trees, full filling all the requirements of various statutory/ environment authorities to the entire satisfaction of concerned authorities, grading of work area. Shifting of all obstruction within the ROU/ Pipeline route alignment viz. electrical lines/ poles, telephone line / poles, etc. coordination with concerned authorities and obtain permissions from these authorities. | Item5
6 | Trenching to all depths by excavation in all types of soils including soft/ hard rock and different type of pavement / footpath / roads etc. including rock breaking, chiselling or otherwise cutting etc. as required and storing excavated soil, reusable materials at designated area as directed by Engineer in charge and to a width to accommodate the Steel pipeline as per the relevant standard/ specification etc. [The minimum depth of the top of pipeline shall be 1.2m measured from top of pipeline coating to the top of undisturbed surface of the soil or as per SCC/ OISD - 141 / 226, whichever is higher]. Dewater of trenches if required as per site condition. | Item6
7 | Carrying out repairs of pipe defects/ replacement in case of irreparable defects and repairs of defects of pipe coating not attributable to Owner including defects/ damages occurring during transportation / handling. | Item7
8 | Stringing of line pipes along pipeline trench / ROU on straw / sand / soft soil bags including supply of bags and its filling materials. | Item8
9 | Checking, cleaning, aligning, bending, cutting and bevelling (as required) of pipes for welding and field adjustments including pipe fittings, welding, carrying out non-destructive testing of welds as required including 100% radiography by X-ray and providing all requisite equipment, labour, supervision, materials, films, consumables, all facilities and personnel to process, develop, examine and interpret radiographs and other tests as required, carrying out repairs of weld joints found defective by Engineer-in-Charge, carrying out re-radiography and other tests as required on repaired joints. | Item9
10 | Carrying out installation of carrier line pipe at all minor crossing viz. carttrack, pathway, water bodies etc. at designated depth by open cut (except at crossing by HDD method). | Item10
11 | Carrying out installation of carrier line pipe in the casing pipe at cased crossing (excluding installation of casing pipes which is covered separately). | Item11
12 | Coating of field weld joints, long radius bends (R=3D), elbows, buried fittings and valves etc. including supply of coating materials etc. (i.e. heat shrinkable sleeves and high build epoxy etc.) as per PJS & Technical Specification compatible with 3 layer PE coating material of the line pipe. | Item12 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
13 | Counting the number and type of trees cut in presence of DFO/concerned authorities and keeping record thereof, stacking and handing over of all cut tress. | Item13
14 | Installation / lowering the pipeline in trench to required depth as per PJS, Techanical Specification & drawings, supply & placement of 1.0mm thk. HDPE Yellow colour warning mat,RCC tiles (300 mm width x 50 mm thick) over the pipeline in same trench along the complete route as per standard drawings, data sheets & technical specifications, padding around pipeline as per Standard Drg. no. MNGL/Plng./Steel/03 with suitable soil duly approved by EIC including supply of padding material, backfilling and its compaction to the satisfaction of concerned authorities with excavated earth / borrowed select soil including supply of borrowed select soil duly approved by EIC before backfilling and make ready for restoration to be done by Onwer / concerned authorities. | Item14
15 | Supply and installation of slope breakers, wherever required or, as directed by Onwer / Engineer–in–charge. | Item15
16 | Crossing the all-foreign pipeline / HT line / cable / any other utilities etc. with necessary concrete / HDPE sheet protection including coordination with all agencies and obtaining NOC | Item16
17 | Supply and installation of bank protection alongwith backfill materials duly approved by EIC for pipeline trench and banks falls under minor water body crossing as per technical specification & Std. Drg. No. MNGL/Plng./Steel/28, wherever required or, as directed by Onwer / EIC. | Item17
18 | Training and diversions of streams in steep slope area, wherever required. | Item18
19 | Carrying out air cleaning, pigging, flushing, cleaning and hydrostatic testing of complete pipeline with required quantity of corrosion inhibitor including pre-testing of designated sections complete as per specification and approved by Engineer–in–charge to specified pressures indicated elsewhere and duration after stabilization as per specification, providing all equipment, pumps, fittings, instruments, dead weight tester, pressure recorder, thermocouples etc., and services, supervision, labour, consumables, water including supply of corrosion inhibitor, air, etc. as required, locating of leaks and rectification of defect attributable to Contractor (rectification of defects in linepipe material not attributable to contractor shall be paid separately as per other item of schedule of rate), re-testing after rectification, dewatering after successful completion of hydrotesting of entire section and as per specification | Item19
20 | All tieing-in, including the tie-in(s) of the pipeline with the adjacent sections of pipeline including cutting of test header, rebevelling as required, radiography and other NDT examination, joint coating as per specification. | Item20
21 | Final clean-up of right-of-use or area disturbed by contractor during their construction activities for laying of pipeline works and disposal of debris and surplus material to designated disposal areas and backfilling of trench and compaction of the same as per satisfaction of Owner and / Or as directed by Engineer–in–charge. | Item21
22 | Installation of all burried valves (except extended stem valves) inside the valve pit and making provision to operate the valve. | Item22 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
23 | Preparation of as-built drawings, pipe-books (1 set of tracing on polyester film and 6 sets of as-built drawings and 1 soft copy and 6 hard copies of pipe book) All the works shall be executed in accordance with the provision of contract including carrying out all temporary/ ancillary/ auxiliary works required for the performance of the works and all other acts, deeds, matters and things necessary to make the pipeline ready for precommissioning activities. | Item23 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
24 | Raking up of hard surface of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. Payment for cutting of hard rock, if any, is covered unders SOR no. 76 | Item24 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
25 | Specified dia Thk (mm) Material Coating Type Length of each pipe (mm) NB | Item25 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
26 | 305 (approx.) 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item26 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
27 | Note: This item shall be applicable for the underground steel grid main pipeline & branch pipeline, barred tees, insulating joints, bends, flanges & fittings, accessories etc. (i.e. including arrangement for making provision for tap-off on proposed steel grid main pipeline) and aboveground approach pipeline upto Insulating Joint (excluding installation of aboveground insulating joint) for various stations. | Item27
28 | Items except above are covered separately. The lengths of pipelines are tentative. | Item28 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
29 | Permission Liasioning /Follow-up | Item29 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
30 | Liasioning & follow up for Permission with all the concerned authorities & boards viz Railways, NH, PWD, MIDC, Local Municipal, Panchyat, Electricity, REC, RES, Sewage water, Drinking water, Forest, Social Forestry, Owners of OFC, Traffic, Law & Order, Fire Brigade, Private Land Owner etc. for entire pipeline length and associated terminals (like SVs, tap-offs) alongwith associated work as per tender. | Item30 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
31 | Laying of RCC Tiles | Item31 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
32 | Providing single layer of RCC Tiles with supply of RCC Tiles to entire width of trench above Warning Mat placed in trench over the laid pipeline as per standard drawing, specification and instruction of Owner. (Rate to include cost of all labour, tools, tackles, equipment, hire charges & supply of all materials, etc.) | Item32
33 | For width of 12" pipeline trench | Item33 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
34 | Barricading to comply with HSSE | Item34 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
35 | Steel barricading of the trenches Cautionary Sign Boards and lighting arrangement shall be provided as per attched drawing no.MNGL/Plng./steel/04. The rates include barricading of trenches along with sign boards, lighting etc. and maintain the same till the back filling of the trench. Rates will be payable per metre of BARRICADING PROVIDED. If proper barricading is not provided, MNGL will barricade the trenches at the risks and costs of the CONTRACTOR and will levy penalty of twice the rate per unit for the relevant section of the pipeline apart from other actions as per contract. | Item35 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
36 | RESTORATION OF ROADS Restoration of asphalt / concrete / red stone roads / pavement/Footpath/Paver block including compaction of soil, to original condition as per requirement and to the entire satisfaction of EIC and / or concerned Owners having jurisdiction for following thickness. | Item36 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
37 | Restoration of Asphalt road upto 10 cm thickness | Item37 | 700 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
38 | Restoration of Asphalt road beyond 10 cm upto 20 cm thickness | Item38 | 200 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
39 | Restoration of Concrete road upto 10 cm thickness | Item39 | 800 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
40 | Restoration of red stone road / footpath / pavement/ Paverblock upto 4 cm thickness | Item40 | 900 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
41 | BORROWED SELECT SOIL FOR BACKFILLING Additional work over and above item 1.0 for supply of specified and approved quality of borrowed soft graded soil / sand in place of available excavated material and / or other suitable soil as per applicable standards / specifications, including backfilling of excavated trench for specified length after laying and padding of pipeline, including transportation of such special backfill material over all distances, complete. | Item41 | 900 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
42 | CROSSING OF STEEL PIPELINE BY OPEN CUT | Item42
43 | Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insatllation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed. | Item43
44 | Road Crossing By Open Cut Method Road Crossings at various locations by Open cut Method as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item44 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
45 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method | Item45 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
46 | Water body Crossing By Open Cut Method water/ canal/ nallah/ drain/ channel Crossings at various locations by Open cut Method as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item46 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
47 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method | Item47 | 90 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
48 | Note: Laying of the pipeline by the approved method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item48
49 | Backfilling of the Road/water/ canal/ nallah/ drain/ channel Crossings/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority. | Item49
50 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item50 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
51 | CROSSINGS/LAYING ALONG THE ROAD BY HDD METHOD | Item51
52 | Complete work of the any crossing (between the limits are defined as approved drawings) by HDD method including "Receiving and taking over" owner supplied three layer PE coated line pipes from Owner's designated place to issue/ dump site(s) and transportation to Contractor's stock yard/ work shop/ work site including all handling loading, unloading, aligning etc. supply of all Contractor supplied material, manpower, equipment, other resources and aquiring the required land for storage, fabrication inclduing string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type Heat Shrink Sleeve and repair of pipeline coating with special repair patch materials as per specification,pre-testing etc. of complete string made for crossing access for Contractor etc and execution of, but not limited to, following works in accordance with specifications scope of work and instructions of Engineer-in-charge and as per all provision of Contract Document. | Item52
53 | Pre-construction surveys based on site visit, collection of historical data from irrigation/ concerned department including design & calculation and detail engineering and making of crossing drawing for getting their approval from concerned Authority/ Engineer-in-charge, getting work permit/ NOC for water crossings/ road crossings as well as utility crossings (if any) encountered during crossing prior to start the execution of work. | Item53 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
54 | Directional drilling to required depth from top of road including maintenance of drill hole in all types of strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) at all depth to accommodate the pipeline at all conditions encountered during rail/ road crossing by approved HDD methods for providing minimum cover specified in code/ specification or the actual depth as decided by concerned authority, whichever is more. | Item54 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
55 | In case of water crossing, drilling to the required depth on the banks and bed including maintenance of drill hole in all types of soil strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) all depth to accommodate the pipeline a by HDD methods for providing with minimum cover over top of the pipe at all point across the maximum possible width of water bed (as per drawing) either 1.5 mtrs. below the predicted scour profile expected during the life time of the pipeline or 2.5 mtrs. below the available lowest firm bed (if scour profile/ depth not available) of the water crossing by ascertaining bed level upto 50 mtrs. both the side from crossing location or the actual depth as decided by concerned Authority/ Engineer-in-charge whichever is more. | Item55 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
56 | Laying of the pipeline by the approved HDD method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints with special type Dirax Heat Shrink Sleeve or equivalent and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item56 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
57 | Backfilling of the ditch/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority and all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specification, approved drawings, calculations, methods and to the satisfaction of Engineer-in-charge and/or as directed by concerned Authority. | Item57 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
58 | Post installation hydrotest dewatering and tie-in with pipeline at either side of crossing/banks etc. | Item58 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
59 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item59 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
60 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 by HDD Method . | Item60 | 120 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
61 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item61 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
62 | Installation of carrier pipes by rock drilling for Road/water/Canal/ nallah/ drain/ channel/along the road, or wherever required in all types of hard rock. It includes survey of the underground utilities, submission of profile for approval, execution of the work as per the standard procedure, including , excavation of the pits, insertion/pulling of the carrier pipe, removal of malba, subsequent backfilling and restoration of the facility crossed as per original condition, including supply of all other materials, equipment, consumables, manpower etc including string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type of Heat Shrink Sleeve (Direx) and repair of pipeline coating with special repair patch materials as per Specification, pre-testing etc. of complete string made for crossing/ laying access for Contractor etc. and execution of, but not limited to, following works in accordance with specifications and instruction of Engineer-in-Charge and as per all provision of Contract Document. Balance activities as defined in SOR Item of open trench. Note:The length of HDD mentioned is tentative and may vary to the considerable extent depending upon requirements as per site conditions. The length mentioned in SOR is indicative for all the crossing to be done by HDD, numbers and locations shall be decided by Engineer-in-Charge depending upon site condition. Payment for the length of final tie-in carrier pipeline string with mainline laid by HDD are inclusive in this above item rate. No separate payment shall be made under other clauses mentioned elsewhere. Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item62
63 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 by HDD Method . | Item63 | 90 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
64 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item64 | 90 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
65 | Note: (i) Crossing width & Actual string length for HDD shall vary as per design calculations & site condition so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. | Item65
66 | (ii)Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item66
67 | (iii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by HDD method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item67
68 | (iv) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossing at different locations. | Item68
69 | (v) The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. | Item69
70 | Note: (i) Quantity mentioned under item nos. 44, 46 are indicative only for different location of roads/water/ canal/ nallah/ drain/ channel Crossings. (ii) Actual length & width of individual crossing and cover from top of casing pipe/ carrier pipe string may vary depending upon site condition, approved crossing drawings, specifications etc. and / or as decided by Engineer-in-charge/ Concerned Authority. | Item70
71 | (iii) Payment for supply & installation of Zinc ribbon anode and its design excluded from above item and covered elsewhere in the SOR. (iv) Payment for the length carrier pipeline string inserted in casing pipe laid by Boring are covered separately and shall be paid under other clauses mentioned elesewhere in the SOR. | Item71
72 | Excavation beyond 1.5m depth in case of crossing of utilities/ drain/ culverts etc. through open cut upto the following depth (including restoration of the damaged area to its original condition and satisfaction of the Engineer-in-charge / concerned authorities) : - | Item72 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
73 | In all type of surface (Kachha/ built-up surface / Hard surface) of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. The other activities are as per SOR 1.1. Payment for cutting of hard rock, if any, is covered unders SOR no. 76 | Item73
74 | Deeper than 1.5 m & upto 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item74 | 600 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
75 | Deeper than 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item75 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
76 | Excavation of hard rock | Item76
77 | Excavation of hard rock wherever hard rock of single piece exceeding 1.0 m in length removable by pneumatic chisel/ drill as per direction of EIC. | Item77 | 3800 | Cub. M |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
78 | REPAIR OF COATING DEFECTS (NOT ATTRIBUTED TO CONTRACTOR) | Item78
79 | Repair of Holiday in Coating (Noted and recorded at the time of "receiving and taking over") Supply of all coating repair materials as per requirements of specification to be compatible with line pipe coating material, supply of all consumables, utilities, equipments and all manpower required, pipe cleaning and surface preparation, repairing of coating defects (resulting in holiday) and testing including all handling, transportation, etc. for line pipes, performing all works necessary for the completion of the works stirctly in accordance with relevant specification and instructions of Engineer-In-Charge. This rate shall be applicable per sq. cm of the exposed steel area exposed steel area. | Item79 | 2200 | Sq. cm. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
80 | PERMANENT MARKERS Supply, fabrication and installation of all types of permanent markers along the route including all associated civil works such as excavation in all types of soil, construction in all types of soil, construction of pedestals and grouting with concrete, clearing, supply and application of approved colour and quality of primer and paint, stencil letter cutting for numbers, direction, change etc., restoration of area to original condition and performing all works as per drawing, specification and instruction of engineer-in-charge. | Item80
81 | Pipeline RCC boundary / route marker as per drawing | Item81 | 120 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
82 | Pipeline warning markers with post & foundations | Item82 | 40 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
83 | Pipeline direction marker with post & foundations | Item83 | 25 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
84 | Pipeline KM with post & foundations | Item84 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
85 | HOOK -UP | Item85
86 | Hook-up of proposed pipeline by welding of final tie-in-joint with any existing laid pipeline portion of river X-ing ,existing Tap-off & battery limit of section IV including Hook-up point of the existing pipeline to be made ready for welding by cutting of flanges / valves / headers at all depth in all type of soil etc. Venting of N2 / gas / gas mixture as required purging of N2 Gas (if required), rebevelling as required, radiography and other NDT examination, joint coating as per specification.Contractor shall supply of all consumables, manpower, machinaries, materials, N2 gas etc. and carry out all works as per the provisions of Contract document and instructions of Engineer-in-charge. | Item86
87 | For 12" NB | Item87 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
88 | PRE-COMMISSIONING AND ASSISTANCE IN COMMISSIONING OF PIPELINE SYSTEM Swabbing, drying, purging with nitrogen of the complete pipeline network and the associated facilities being installed to the specified acceptance criteria, carrying out pre-commissioning works, providing assistance during the complete duration of commissioning operations for entire pipeline network system including supply of all equipment, man-power, consumables (including pigs & nitrogen required for purging with maintaining nitrogen column of mininum 10% of pipeline geometric volume) materials for all temporary works and performing all associated works, complete as per the relevant specifications, other provisions of Contract document and instructions of Engineer-in-charge. | Item88
89 | For 12" NB Pipeline | Item89 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
90 | IDLE TIME PRESERVATION OF PIPELINE Preservation of complete pipeline and associated facilities forming part of the pipeline as per Bid document and its maintenance including supply of all consumables, all equipment, manpower, etc. complete as per the requirements of specifications, other provisions of Contract document and instructions of Engineer-in-charge. Note : Owner reserves the right to exercise either or none of the rates below. | Item90
91 | By filling and pressurizing with nitrogen to a pressure of 2 bar(g) for a period of 3 months. | Item91 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
92 | For 12" NB Pipeline | Item92 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
93 | For every additional period of one month or part thereof | Item93 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
94 | For 12" NB Pipeline | Item94 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
95 | RCC VALVE PITS All civil works including supply of all materials, excavation of pit, piping supports including all PCC and RCC works for valves pits including pedestals with insert plates as required sealing of pipe at valve pits, providing cover etc. and finishing , clean-up and restoration of site, filling and grading of area around valve station for avoiding any local flooding of area, as per typical drawing and specification enclosed and instructions of Engineer-in-charge. In this item, instead of Brick Work, RCC will be done | Item95 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
96 | Valve Pit of Size 2m x 2m | Item96 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
97 | SUPPLY OF ASSORTED PIPE, FITTINGS AND FLANGES Complete works of supply of pipes, flanges & fittings for aboveground & underground installation including all taxes, duties, transportation and inspection charges but not limited to, the following items in accordance with PMS (piping material specification), relevant specifications & drawings indicated in job specification under SCC (technical) and instructions of Engineer-in-charge and as per all provisions of the CONTRACT DOCUMENT. - Handling including lifting, transportation from Contractor Stores to CONTRACTOR's workshop for fabrication and/ or to work site for field fabrication and erection for all piping items supplied by Contractor. | Item97
98 | Carbon Steel Pipe (A 106, Seamless B-36.10/ API X 52 ) | Item98
99 | Size Rating/ Schedule | Item99 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
100 | 2" NB, BE Sch. 80 | Item100 | 55 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
101 | 1" NB, PE Sch. 80 | Item101 | 38 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
102 | ¾" NB, PE Sch. 160 | Item102 | 36 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
103 | Flanges | Item103
104 | Weld Neck (B-16.5, 300# A105,125 AARH, Serrated finish) | Item104
105 | Size Rating/ Schedule | Item105 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
106 | 2" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item106 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
107 | Blind Flanges (B-16.5, 300# A105,125 AARH Serrated) | Item107
108 | Size | Item108
109 | 2" NB, RF | Item109 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
110 | Elbow (Seamless) | Item110 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
111 | 90° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item111
112 | Size Rating/ Schedule | Item112
113 | 12" NB 300# | Item113 | 24 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
114 | 45° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item114 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
115 | Size Rating/ Schedule | Item115
116 | 12" NB 300# | Item116 | 24 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
117 | 90° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item117 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
118 | Size Rating/ Schedule | Item118
119 | 12" NB 300# | Item119 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
120 | 45° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item120
121 | Size Rating/ Schedule | Item121
122 | 12" NB 300# | Item122 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
123 | 22½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D) Min Thickness 6.4mm | Item123 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
124 | Size Rating/ Schedule | Item124
125 | 12" NB Sch. Std. | Item125 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
126 | 11½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D), Min Thickness 6.4mm | Item126
127 | Size Rating/ Schedule | Item127
128 | 12" NB 300# | Item128 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
129 | Tees (Seamless) | Item129
130 | Equal Tee (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item130
131 | Size Rating/ Schedule | Item131
132 | 12" NB x 12" NB x 12" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item132 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
133 | 2" NB x 2" NB x 2" NB Sch. XS | Item133 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
134 | Weldolet and Sockolet | Item134
135 | Weldolet (MOC A105 & DIM. MSS SP 97) | Item135
136 | Size Rating/ Schedule | Item136
137 | 12" NB x 2" NB Sch. 80. | Item137 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
138 | Sockolet (MOC A105 & DIM. MSS SP 97) | Item138
139 | 12" NB x 3/4" NB #6000 | Item139 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
140 | Butt Weld Disc End Cap (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item140
141 | Size Rating/ Schedule | Item141
142 | 12" Sch. Std. | Item142 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
143 | Fabrication & Installation of Underground Valve Assembly | Item143 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
144 | 12"NB Isolation Valve/tap-off assembly as per Drg. No. MNGL/Plng./Steel/40 | Item144 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
145 | Note: | Item145 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
146 | For all the supply items mentioned above, procurement shall be made as per enclosed Data Sheets and respective technical specification, after due approval of Engineer-in-charge. | Item146
147 | The quantities mentioned above are tentative and quantities for above supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item147
148 | PLANT PIPING (ABOVEGROUND) Fabrication and testing of carbon steel piping and fittings, valves, IJ, including supply of all consumables, equipment, manpower, and other resources and execution of job as per instruction AIC/EIC.Transportation of all piping items from Owner's and/ or Contractor's storage point to work at site/ workshop as applicable, complete work of fabrication, erection, painting, testing of pipes, flanges and fittings and making ready for further Commissioning / Start-up of carbon steel piping of all sizes and ratings including supply of all consumables, equipment, manpower and other resources and execution of, but not limited to, as per all provisions of the CONTRACT DOCUMENT. | Item148 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
149 | Fabrication including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site, cutting, edge preparation, inclusive of grinding the edges of pipes, fittings, flanges, reducers etc. to match with the matching edges of uneven thickness, wherever required, fit-up, welding of pipes and fittings like elbows, tees, reducers, weldolets, sockolets, Valves, IJ etc. flanges, vent and drain point connection, Radiography and NDT of all joints etc, including providing stubin connections, fabricated fittings and reinforcement pads etc., as required. | Item149 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
150 | Erection of pipes of all types and thickness at all elevations, connecting with equipment nozzle, aligning, installation and carrying out connected activities for all types of valves, all online instruments and fittings of all sizes of elbow, reducers, tees, flanges, blind flanges, spectacle blind flanges, branch connection / tapping for pressure gauges, including installation of gaskets and bolts. | Item150 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
151 | Erection including prior cleaning, lifting, placing on pipe sleepers and supports, overhead on racks, skids and at all elevations including installation and carrying out connected activities for all types of valves including supply and fixing of gaskets, studs/ bolts, nuts wherever required for all sizes, levelling, aligning, joining of flanges, blind flanges, connecting with equipment, nozzles, strainers, tie-in with existing piping/facilities, etc. tapping for inline instruments like pressure gauges, thermowells, sample connection, etc. | Item151
152 | Hydro testing of the piping job shall be conducted at pressure mentioned in specification for a period of 4 hours by using de-mineralised water, to check its strength. No visible leakages shall be detected during the test. Testing shall be conducted as per tender specification. | Item152
153 | Preparation of final bill of material based on piping GADs. | Item153
154 | Preparation of isometric and fabrication drawings. | Item154
155 | Carrying out Non-destructive testing as required | Item155
156 | Painting of entire system (including aboveground all pipes fittings, flanges and accessories) as per specifications suitable for highly corrosive area environment including supply of approved paints and primers, application of primer and paints, indentification lettering/ numbering, colour coding, etc. as specified including rub down & touch up of shop primer or scrapping of shop primer wherever required by COMPANY and providing scaffolding for all heights etc. | Item156
157 | Cleaning and flushing by water/ compressed air, testing of the systems including hydrostatic, pneumatic and any other type of testing as specified, draining, drying by compressed air/other methods approved by COMPANY. | Item157
158 | Precommissioning & making operational all piping system and equipments. | Item158 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
159 | Commissioning Contractor scope shall provide all necessary assistance in term of supply of man-power, equipment, tools and tackles required amount of nitrogen for purging of entire terminal piping system including equipments etc. to the company during commissioning activities. | Item159 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
160 | Completion of all such work in all respects as per scope of work and as per drawings, specifications and instructions of the COMPANY and keeping the system ready in all respects for further commissioning and start up. | Item160 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
161 | Hook-up works (with client/ consumer piping at battery limits): | Item161 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
162 | Complete Carbon Steel aboveground Piping Work with painting including all fittings, flanges and supply of all required gaskets, studs bolts & nuts etc. and Any other work and material required for the completion of the work and not covered above and desired by EIC shall be in the scope of contractor | Item162 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
163 | Carbon Steel Pipe (ASTM A 106, Seamless B-36.10 / API X 52) | Item163 | 150 | inch Dia |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
164 | 1) Pipe Specification and thickness may vary depending upon availability of pipe. No extra payment shall be made for this. 2) All butt welded fittings & flanges end shall generally match with connecting pipe wall thickness. However, in case of misalignment, Contractor shall have to do end preparation without any extra cost. 3) All o-lets less than 2" NB size, all sizes of coupling and nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under erection rate. | Item164 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
165 | Aboveground installation of Insulating Joint & Valves etc. Handling including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site and installation of all types of valves, insulating joint including assembly of valve accessories, (if any) by bolting, threading or welding, supply and insertion of gaskets, nuts & bolts, nipples, etc. at all elevations of pipe sleepers, supports or overhead on racks, equipments nozzle, skid & painting etc. supply of all consumables, manpower, equipment, etc. for completion of all works as per scope of work and as per drawings, specifications and instructions of Engineer-in-charge including servicing/ cleaning of valve wherever requried. | Item165 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
166 | 12" NB, 300# - Insulating Joints | Item166 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
167 | STRUCTURAL WORKS | Item167 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
168 | Supply of erection of single leaf mild steel gate 2.5m high with mesh upto 2m height and barbed wire fencing and 2m wide complete in all respect including painting as per TS on all MS items, all works as per specification and drawings excluding foundations and RCC beams. | Item168 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
169 | Supply of all materials, fabrication and erection of chain link fencing 2.5m high with mesh up to 2m height and barbed wire fenching complete in all respects including painting as per TS on all MS items, all works as per specification and drawings excluding foundation and RCC beams. | Item169 | 150 | RM |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
170 | Pipe Supports & Other Structures | Item170 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
171 | Supply, fabrication and erection of all types of pipe supports like clamps, saddle, guide stops, cradles, turn buckles, anchors, T-posts; stockade/ trestle and pipe bridge for overhead piping; frames for canopy, approach ladders and platforms, crossover, cable tray supports, etc. including painting suitable for highly corrosive area as per specification labour and supervision & complete work as per drawings, specifications and instruction of Engineerqw-incharge. (Bolts, nuts, washers, U-clamps etc. for supporting shall be supplied by the Contractor within the rates quoted. These items will not be measured and paid seperately). The work is to be completed in all respect as per scope of work and specification. | Item171 | 250 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
172 | Notes: | Item172 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
173 | The quantities indicated are estimated values and hence are approximate. Final payment will be made based on actual quantities to be certified by the Purchaser. | Item173
174 | The cost of MS bolts (permanent and service(, washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants etc., as required for the work shall be deemed to be included in the quoted rates. | Item174 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
175 | All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accrodance with time schedule, are deemed be included in the quoted rates. | Item175
176 | CIVIL WORKS | Item176
177 | Site Grading Excavation in earth and filling to the grades and levels shown in the approved drawings in all kinds of conditions including for Road embarkments, using approved quality good earth from designated borrow area, for all heights and depths including clearing and stripping (min. 150mm) of the area marked for filling, taking spot levels, consolidating the exposed natural soil surface, excavating the earth from borrow area loading, transporting & unloading, spreading in layers not exceeding 150mm thickness, breaking clods, watering (if reqd.), ramming and compacting by manual/ mechanical means to give minimum 92% of modified Proctor's density of earth, testing & dressing including disposal of all unserviceable material all complete as per specifications and directions of Engineer-in-charge. | Item177 | 200 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
178 | (Rate to include cost of all labour, tools, tackles, equipment, hire charges, cost of borrow earth by way of royalties, right of way, cess etc., as applicable with all bye works and sundry works). | Item178
179 | Plain Cement Concrete Supplying and laying plain cement concrete (including shuttering of required) in all types of concrete works including levelling courses below foundation, substructure, superstrcuture, chambers, cable tranch, under floors and any other locations, at all leveies as per drawings, specifications and directions of the Engineer-in-charge. | Item179
180 | PCC 1:2:4 1 Cement : 2 Coarse sand : 4 stone aggregate 20mm nominal size. | Item180 | 500 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
181 | Reinforced Cement Concrete Providing and laying reinforced cement of grade M-20 with 20mm and down grade crushed stone aggregate in all types of structures like foundations, pedestals, pedestal bases, pipe supports, sleepers cable trench inlcuding constrcution joints, bitumen painting on surface in contact with soil, providing and fixing reinforcing steel, shuttering, inserts, finishes etc. at all depths and heights complete as per drawings, specifications and direction of the Engineer-incharge. | Item181 | 400 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
182 | Rate to include cost of all labour, tools, tackles, equipment, hire charges, supply of all maerials such as minimum 43 grade cement including sulphate resistant cement for substructures, R/F steel, Inserts, bolts, conduits, bitumen, other minor constrcution materials, shuttering, stanging, earthwork in excavation and backfilling using serviceable earth in all conditions, shorting bailing and pumping out water, testing of concrete, curing etc. with all bye works and syndry works. | Item182
183 | TEMPORARY CATHODIC PROTECTION SYSTEM | Item183
184 | Design, detailed engineering, supply, installation, testing and commissioning of the temporary Cathodic protection system using Mg/ Zn galvanic anodes to protect the external surface of 3 LPE coated entire 5.5 km (approx.) long steel pipeline network against corrosion for design life of minimum 1 year or till commissioning of PCP system whichever is later as per standard specification No. MNGL/Steel/TS/15 for temporary cathodic protection system. Scope shall also include but not limited to the following for completion of jobs: | Item184 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
185 | Measurement of soil resistivity along the right of way of the main pipeline route as per specification for design & installation of anodes. | Item185
186 | Collection of additional data related to cathodic protection along the right of way of pipeline as per specifications. | Item186 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
187 | Supply, installation, testing & commissioning of one set of spark gap arrestor with 2 plate Zinc grounding cell of 20 kg net weight each across each insulating joint as per specification. | Item187
188 | Supply, installation, testing & commissioning one set of polarisation cell with zinc anode at all high tension (66KV or higher) electrical power transmission line/Equipment crossing or running parallel to the pipeline for grounding purpose as per specification. The rating shall depend upon anticipated fault current & ground bed resistance at the location of installation. However, the rating of polarisation cell (krick) shall not be less than 5 KA & number of 20 kg net weight zinc anode shall not be less than two. | Item188
189 | Supply & installation of Zinc Ribbon Anodes at 4-8 O’Clock position in the interval of 2 metre (max.) on carrier pipes at all cased crossings i.e. railways/ roads etc. | Item189 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
190 | Monitoring of the protection system for 6 months. | Item190
191 | All civil/ structural works related to TCP system including supply of bricks, cement & steel etc. required for completion of the system. | Item191 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
192 | For 12" | Item192 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
193 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item193 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
194 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item194 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
195 | FIELD INSTRUMENTATION | Item195 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
196 | PRESSURE INSTRUMENTS | Item196
197 | Supply , Installation of Pressure Gagues and their accessories inclusive of supply of necessary piping materials and tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/ manifolds & hydraulic testing (exclusive of calibration of instruments) as per installation standard attached elsewhere in Tender Document and Supply as per Data Sheet No.MEC/23K8/05/E5/I/001/DS-PG. Give breakup of supply and Installation rate. | Item197 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
198 | CALIBRATION | Item198
199 | Calibration of the instruments listed below including removal of instruments from pre-installed locations like panels, enclosure racks, fields etc. and refixing them back in respective/ required places, providing equipments, necessary test jigs, instrument air and all consumables. Calibration reports shall be prepared and to be submitted to the Purchaser/ Consultant. | Item199
200 | Pressure Gauges | Item200 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
201 | Note: | Item201 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
202 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item202 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
203 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item203 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
204 | PIPING WORKS FOR SECTIONALISING VALVE STATION-CUM-TAP-OFF POINT All works for fabriaction and installation of all piping above ground at all elevations and below ground at all depth for Sectionalising Valve Station alongwith preparation of construction drawings duly approved by EIC, in all type of terrains and soils including transportation and handling of all Owner supplied materials i.e. extended stem butt welded sectionalising gas actuated ball valve, other types of valves, line pipes for mainline, 4" NB pipe for all branch line including ventlines from Owner's designated place(s) of issue to work site. | Item204 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
205 | Contractor shall supply all required size & type of piping material like pipes, fittings & flanges etc. as per PMS alongwith 2" NB pipe for all branch line & vent line (wherever required) including supply of all consumables, manpower, machinaries, materials etc. and carrying out all mechanical works of underground and above ground piping including fabrication, welding, nondestructive testing of welds, weld repairs/ retesting, cleaning/ flushing, pre-hydrotesting & hydrostatic testing, dewatering, functional testing, cutting of mainline and bevelling (if required) | Item205
206 | assembly, including radiography of tie-in joints, corrosion, coating and external painting as required, installation of instruments like pressure/ temperature instruments/ gauges alongwith complete SS Tubing works including supply of SS Tube and thier accessories etc., as required, obtaining all statutory clearances, approvals and permissions for the works (wherever required), making of valve pit (for detail refer relevant drawings) for SV Stationscum- tap-off points enclosed with tender filled with sand, excavation and filling in all types of soils including soft/ hard rock for installation of piping/ pipe supports providing pipe supports, area fencing and gate including all associated civil and structural works; painting, finishing, clean-up and restoration of site; preparation of as-built drawings, documents and project records and performing all works as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge. In this item, instead of Brick Work RCC will be done | Item206 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
207 | Type - I SV Station on 12" Pipeline | Item207 | 1 | Lumpsum for each |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
208 | Note: i) Work under above items are exclusive of all works associated with main pipeline covered under Item No. 1.0 above. ii) All civil/ structural works including area fencing and gate, valve pits except for piping support will be paid separately as per unit rate provided elsewhere in the SOR. iii) All coupling, nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under above item rate. | Item208 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
Total in Figures | [51 empty] | 0 | 0 | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## BoQ14 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR | [49 empty] | 1
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Maharastra Natural Gas Ltd.,Pune
Name of Work: TENDER FOR LAYING & CONSTRUCTION OF 12” NB X 6 KM U/G STEEL PIPELINE NETWORK & ASSOCIATED WORKS FROM NEAR HOTEL TULJA BHAVANI, MANTHA ON NH 548C TO NEAR NYARA PUMP, KHARI ARDA (Section No-14)
Tender No: MNGL/CP/2024-25/109
Do you want to quote for this sheet ? |  |  | Yes
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE / SCHEDULE OF RATES (SOR) (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Rate inclusive of all taxes and duties except Goods & Service Tax (Rs.) | Per Unit Goods & Service Tax (GST) In % (To be entered by the Bidder) | GST in Rs. | Unit rate inclusive of all taxes & duties including GST (Rs.) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | CARBON STEEL PIPES | Item1
2 | PIPELINE LAYING / INSTALLATION in all type of surface (Normal/built-up surface) "Receiving and taking over" as defined in the specifications, handing, loading, transportation and unloading of Owner supplied 3-Layer PE coated linepipes from Owner's designated stack-yard to Contractor's stock yard/workshop/work-site including preliminary activities, preparation of drawings, wherever required for crossing etc. including handling, stacking, stringing on the pipeline Right-of-Use/ pipeline route alignment, carrying out inspection of company supplied materials including linepipes at the time of taking over, laying/ installation of coated linepipes, associated burried valves, barred tees, insulating joints, flanges & fittings of all sizes, thickness & ANSI class rating and accessories as per specification wherever required depending on site condition including execution of all works, "taking over", handling , including loading and unloading, transportation of Owner supplied materials other than linepipe from Owner's designated place (s) of issue to work site, | Item2 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3 | additional lands required for Contractor's storage, fabrication, access for construction, procurement and supply of all materials (except Owner supplied materials), consumables, equipment, labour and other inputs, carrying out all temporary, ancillary, auxiliary works, aquistion of ROU/ROW for laying of pipeline from HDD Exit and entry point to Tie in Point of existing Pipeline/ ROU, ready for commissioning of pipeline as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge, including but not limited to carrying out the following works: | Item3 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4 | Surveying of route and detours required at the time of execution including marking the same in topographical sheet, preparation of construction drawings showing survey details, and submit same to Owner for review / approval. | Item4
5 | Staking and installation of construction markers, clearing, fencing, grubbing, cutting of trees, full filling all the requirements of various statutory/ environment authorities to the entire satisfaction of concerned authorities, grading of work area. Shifting of all obstruction within the ROU/ Pipeline route alignment viz. electrical lines/ poles, telephone line / poles, etc. coordination with concerned authorities and obtain permissions from these authorities. | Item5
6 | Trenching to all depths by excavation in all types of soils including soft/ hard rock and different type of pavement / footpath / roads etc. including rock breaking, chiselling or otherwise cutting etc. as required and storing excavated soil, reusable materials at designated area as directed by Engineer in charge and to a width to accommodate the Steel pipeline as per the relevant standard/ specification etc. [The minimum depth of the top of pipeline shall be 1.2m measured from top of pipeline coating to the top of undisturbed surface of the soil or as per SCC/ OISD - 141 / 226, whichever is higher]. Dewater of trenches if required as per site condition. | Item6
7 | Carrying out repairs of pipe defects/ replacement in case of irreparable defects and repairs of defects of pipe coating not attributable to Owner including defects/ damages occurring during transportation / handling. | Item7
8 | Stringing of line pipes along pipeline trench / ROU on straw / sand / soft soil bags including supply of bags and its filling materials. | Item8
9 | Checking, cleaning, aligning, bending, cutting and bevelling (as required) of pipes for welding and field adjustments including pipe fittings, welding, carrying out non-destructive testing of welds as required including 100% radiography by X-ray and providing all requisite equipment, labour, supervision, materials, films, consumables, all facilities and personnel to process, develop, examine and interpret radiographs and other tests as required, carrying out repairs of weld joints found defective by Engineer-in-Charge, carrying out re-radiography and other tests as required on repaired joints. | Item9
10 | Carrying out installation of carrier line pipe at all minor crossing viz. carttrack, pathway, water bodies etc. at designated depth by open cut (except at crossing by HDD method). | Item10
11 | Carrying out installation of carrier line pipe in the casing pipe at cased crossing (excluding installation of casing pipes which is covered separately). | Item11
12 | Coating of field weld joints, long radius bends (R=3D), elbows, buried fittings and valves etc. including supply of coating materials etc. (i.e. heat shrinkable sleeves and high build epoxy etc.) as per PJS & Technical Specification compatible with 3 layer PE coating material of the line pipe. | Item12 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
13 | Counting the number and type of trees cut in presence of DFO/concerned authorities and keeping record thereof, stacking and handing over of all cut tress. | Item13
14 | Installation / lowering the pipeline in trench to required depth as per PJS, Techanical Specification & drawings, supply & placement of 1.0mm thk. HDPE Yellow colour warning mat,RCC tiles (300 mm width x 50 mm thick) over the pipeline in same trench along the complete route as per standard drawings, data sheets & technical specifications, padding around pipeline as per Standard Drg. no. MNGL/Plng./Steel/03 with suitable soil duly approved by EIC including supply of padding material, backfilling and its compaction to the satisfaction of concerned authorities with excavated earth / borrowed select soil including supply of borrowed select soil duly approved by EIC before backfilling and make ready for restoration to be done by Onwer / concerned authorities. | Item14
15 | Supply and installation of slope breakers, wherever required or, as directed by Onwer / Engineer–in–charge. | Item15
16 | Crossing the all-foreign pipeline / HT line / cable / any other utilities etc. with necessary concrete / HDPE sheet protection including coordination with all agencies and obtaining NOC | Item16
17 | Supply and installation of bank protection alongwith backfill materials duly approved by EIC for pipeline trench and banks falls under minor water body crossing as per technical specification & Std. Drg. No. MNGL/Plng./Steel/28, wherever required or, as directed by Onwer / EIC. | Item17
18 | Training and diversions of streams in steep slope area, wherever required. | Item18
19 | Carrying out air cleaning, pigging, flushing, cleaning and hydrostatic testing of complete pipeline with required quantity of corrosion inhibitor including pre-testing of designated sections complete as per specification and approved by Engineer–in–charge to specified pressures indicated elsewhere and duration after stabilization as per specification, providing all equipment, pumps, fittings, instruments, dead weight tester, pressure recorder, thermocouples etc., and services, supervision, labour, consumables, water including supply of corrosion inhibitor, air, etc. as required, locating of leaks and rectification of defect attributable to Contractor (rectification of defects in linepipe material not attributable to contractor shall be paid separately as per other item of schedule of rate), re-testing after rectification, dewatering after successful completion of hydrotesting of entire section and as per specification | Item19
20 | All tieing-in, including the tie-in(s) of the pipeline with the adjacent sections of pipeline including cutting of test header, rebevelling as required, radiography and other NDT examination, joint coating as per specification. | Item20
21 | Final clean-up of right-of-use or area disturbed by contractor during their construction activities for laying of pipeline works and disposal of debris and surplus material to designated disposal areas and backfilling of trench and compaction of the same as per satisfaction of Owner and / Or as directed by Engineer–in–charge. | Item21
22 | Installation of all burried valves (except extended stem valves) inside the valve pit and making provision to operate the valve. | Item22 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
23 | Preparation of as-built drawings, pipe-books (1 set of tracing on polyester film and 6 sets of as-built drawings and 1 soft copy and 6 hard copies of pipe book) All the works shall be executed in accordance with the provision of contract including carrying out all temporary/ ancillary/ auxiliary works required for the performance of the works and all other acts, deeds, matters and things necessary to make the pipeline ready for precommissioning activities. | Item23 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
24 | Raking up of hard surface of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. Payment for cutting of hard rock, if any, is covered unders SOR no. 76 | Item24 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
25 | Specified dia Thk (mm) Material Coating Type Length of each pipe (mm) NB | Item25 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
26 | 305 (approx.) 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item26 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
27 | Note: This item shall be applicable for the underground steel grid main pipeline & branch pipeline, barred tees, insulating joints, bends, flanges & fittings, accessories etc. (i.e. including arrangement for making provision for tap-off on proposed steel grid main pipeline) and aboveground approach pipeline upto Insulating Joint (excluding installation of aboveground insulating joint) for various stations. | Item27
28 | Items except above are covered separately. The lengths of pipelines are tentative. | Item28 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
29 | Permission Liasioning /Follow-up | Item29 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
30 | Liasioning & follow up for Permission with all the concerned authorities & boards viz Railways, NH, PWD, MIDC, Local Municipal, Panchyat, Electricity, REC, RES, Sewage water, Drinking water, Forest, Social Forestry, Owners of OFC, Traffic, Law & Order, Fire Brigade, Private Land Owner etc. for entire pipeline length and associated terminals (like SVs, tap-offs) alongwith associated work as per tender. | Item30 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
31 | Laying of RCC Tiles | Item31 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
32 | Providing single layer of RCC Tiles with supply of RCC Tiles to entire width of trench above Warning Mat placed in trench over the laid pipeline as per standard drawing, specification and instruction of Owner. (Rate to include cost of all labour, tools, tackles, equipment, hire charges & supply of all materials, etc.) | Item32
33 | For width of 12" pipeline trench | Item33 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
34 | Barricading to comply with HSSE | Item34 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
35 | Steel barricading of the trenches Cautionary Sign Boards and lighting arrangement shall be provided as per attched drawing no.MNGL/Plng./steel/04. The rates include barricading of trenches along with sign boards, lighting etc. and maintain the same till the back filling of the trench. Rates will be payable per metre of BARRICADING PROVIDED. If proper barricading is not provided, MNGL will barricade the trenches at the risks and costs of the CONTRACTOR and will levy penalty of twice the rate per unit for the relevant section of the pipeline apart from other actions as per contract. | Item35 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
36 | RESTORATION OF ROADS Restoration of asphalt / concrete / red stone roads / pavement/Footpath/Paver block including compaction of soil, to original condition as per requirement and to the entire satisfaction of EIC and / or concerned Owners having jurisdiction for following thickness. | Item36 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
37 | Restoration of Asphalt road upto 10 cm thickness | Item37 | 600 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
38 | Restoration of Asphalt road beyond 10 cm upto 20 cm thickness | Item38 | 200 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
39 | Restoration of Concrete road upto 10 cm thickness | Item39 | 600 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
40 | Restoration of red stone road / footpath / pavement/ Paverblock upto 4 cm thickness | Item40 | 700 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
41 | BORROWED SELECT SOIL FOR BACKFILLING Additional work over and above item 1.0 for supply of specified and approved quality of borrowed soft graded soil / sand in place of available excavated material and / or other suitable soil as per applicable standards / specifications, including backfilling of excavated trench for specified length after laying and padding of pipeline, including transportation of such special backfill material over all distances, complete. | Item41 | 900 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
42 | CROSSING OF STEEL PIPELINE BY OPEN CUT | Item42
43 | Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insatllation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed. | Item43
44 | Road Crossing By Open Cut Method Road Crossings at various locations by Open cut Method as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item44 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
45 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method | Item45 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
46 | Water body Crossing By Open Cut Method water/ canal/ nallah/ drain/ channel Crossings at various locations by Open cut Method as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item46 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
47 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method | Item47 | 90 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
48 | Note: Laying of the pipeline by the approved method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item48
49 | Backfilling of the Road/water/ canal/ nallah/ drain/ channel Crossings/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority. | Item49
50 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item50 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
51 | CROSSINGS/LAYING ALONG THE ROAD BY HDD METHOD | Item51
52 | Complete work of the any crossing (between the limits are defined as approved drawings) by HDD method including "Receiving and taking over" owner supplied three layer PE coated line pipes from Owner's designated place to issue/ dump site(s) and transportation to Contractor's stock yard/ work shop/ work site including all handling loading, unloading, aligning etc. supply of all Contractor supplied material, manpower, equipment, other resources and aquiring the required land for storage, fabrication inclduing string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type Heat Shrink Sleeve and repair of pipeline coating with special repair patch materials as per specification,pre-testing etc. of complete string made for crossing access for Contractor etc and execution of, but not limited to, following works in accordance with specifications scope of work and instructions of Engineer-in-charge and as per all provision of Contract Document. | Item52
53 | Pre-construction surveys based on site visit, collection of historical data from irrigation/ concerned department including design & calculation and detail engineering and making of crossing drawing for getting their approval from concerned Authority/ Engineer-in-charge, getting work permit/ NOC for water crossings/ road crossings as well as utility crossings (if any) encountered during crossing prior to start the execution of work. | Item53 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
54 | Directional drilling to required depth from top of road including maintenance of drill hole in all types of strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) at all depth to accommodate the pipeline at all conditions encountered during rail/ road crossing by approved HDD methods for providing minimum cover specified in code/ specification or the actual depth as decided by concerned authority, whichever is more. | Item54 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
55 | In case of water crossing, drilling to the required depth on the banks and bed including maintenance of drill hole in all types of soil strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) all depth to accommodate the pipeline a by HDD methods for providing with minimum cover over top of the pipe at all point across the maximum possible width of water bed (as per drawing) either 1.5 mtrs. below the predicted scour profile expected during the life time of the pipeline or 2.5 mtrs. below the available lowest firm bed (if scour profile/ depth not available) of the water crossing by ascertaining bed level upto 50 mtrs. both the side from crossing location or the actual depth as decided by concerned Authority/ Engineer-in-charge whichever is more. | Item55 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
56 | Laying of the pipeline by the approved HDD method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints with special type Dirax Heat Shrink Sleeve or equivalent and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item56 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
57 | Backfilling of the ditch/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority and all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specification, approved drawings, calculations, methods and to the satisfaction of Engineer-in-charge and/or as directed by concerned Authority. | Item57 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
58 | Post installation hydrotest dewatering and tie-in with pipeline at either side of crossing/banks etc. | Item58 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
59 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item59 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
60 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 by HDD Method . | Item60 | 400 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
61 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item61 | 250 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
62 | Installation of carrier pipes by rock drilling for Road/water/Canal/ nallah/ drain/ channel/along the road, or wherever required in all types of hard rock. It includes survey of the underground utilities, submission of profile for approval, execution of the work as per the standard procedure, including , excavation of the pits, insertion/pulling of the carrier pipe, removal of malba, subsequent backfilling and restoration of the facility crossed as per original condition, including supply of all other materials, equipment, consumables, manpower etc including string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type of Heat Shrink Sleeve (Direx) and repair of pipeline coating with special repair patch materials as per Specification, pre-testing etc. of complete string made for crossing/ laying access for Contractor etc. and execution of, but not limited to, following works in accordance with specifications and instruction of Engineer-in-Charge and as per all provision of Contract Document. Balance activities as defined in SOR Item of open trench. Note:The length of HDD mentioned is tentative and may vary to the considerable extent depending upon requirements as per site conditions. The length mentioned in SOR is indicative for all the crossing to be done by HDD, numbers and locations shall be decided by Engineer-in-Charge depending upon site condition. Payment for the length of final tie-in carrier pipeline string with mainline laid by HDD are inclusive in this above item rate. No separate payment shall be made under other clauses mentioned elsewhere. Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item62
63 | Crossing of nallah/ drain/ channel//River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 by HDD Method . | Item63 | 300 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
64 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item64 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
65 | Note: (i) Crossing width & Actual string length for HDD shall vary as per design calculations & site condition so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. | Item65
66 | (ii)Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item66
67 | (iii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by HDD method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item67
68 | (iv) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossing at different locations. | Item68
69 | (v) The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. | Item69
70 | Note: (i) Quantity mentioned under item nos. 44, 46 are indicative only for different location of roads/water/ canal/ nallah/ drain/ channel Crossings. (ii) Actual length & width of individual crossing and cover from top of casing pipe/ carrier pipe string may vary depending upon site condition, approved crossing drawings, specifications etc. and / or as decided by Engineer-in-charge/ Concerned Authority. | Item70
71 | (iii) Payment for supply & installation of Zinc ribbon anode and its design excluded from above item and covered elsewhere in the SOR. (iv) Payment for the length carrier pipeline string inserted in casing pipe laid by Boring are covered separately and shall be paid under other clauses mentioned elesewhere in the SOR. | Item71
72 | Excavation beyond 1.5m depth in case of crossing of utilities/ drain/ culverts etc. through open cut upto the following depth (including restoration of the damaged area to its original condition and satisfaction of the Engineer-in-charge / concerned authorities) : - | Item72 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
73 | In all type of surface (Kachha/ built-up surface / Hard surface) of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. The other activities are as per SOR 1.1. Payment for cutting of hard rock, if any, is covered unders SOR no. 76 | Item73
74 | Deeper than 1.5 m & upto 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item74 | 600 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
75 | Deeper than 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item75 | 300 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
76 | Excavation of hard rock | Item76
77 | Excavation of hard rock wherever hard rock of single piece exceeding 1.0 m in length removable by pneumatic chisel/ drill as per direction of EIC. | Item77 | 3800 | Cub. M |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
78 | REPAIR OF COATING DEFECTS (NOT ATTRIBUTED TO CONTRACTOR) | Item78
79 | Repair of Holiday in Coating (Noted and recorded at the time of "receiving and taking over") Supply of all coating repair materials as per requirements of specification to be compatible with line pipe coating material, supply of all consumables, utilities, equipments and all manpower required, pipe cleaning and surface preparation, repairing of coating defects (resulting in holiday) and testing including all handling, transportation, etc. for line pipes, performing all works necessary for the completion of the works stirctly in accordance with relevant specification and instructions of Engineer-In-Charge. This rate shall be applicable per sq. cm of the exposed steel area exposed steel area. | Item79 | 2200 | Sq. cm. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
80 | PERMANENT MARKERS Supply, fabrication and installation of all types of permanent markers along the route including all associated civil works such as excavation in all types of soil, construction in all types of soil, construction of pedestals and grouting with concrete, clearing, supply and application of approved colour and quality of primer and paint, stencil letter cutting for numbers, direction, change etc., restoration of area to original condition and performing all works as per drawing, specification and instruction of engineer-in-charge. | Item80
81 | Pipeline RCC boundary / route marker as per drawing | Item81 | 120 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
82 | Pipeline warning markers with post & foundations | Item82 | 40 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
83 | Pipeline direction marker with post & foundations | Item83 | 25 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
84 | Pipeline KM with post & foundations | Item84 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
85 | HOOK -UP | Item85
86 | Hook-up of proposed pipeline by welding of final tie-in-joint with any existing laid pipeline portion of river X-ing ,existing Tap-off & battery limit of section IV including Hook-up point of the existing pipeline to be made ready for welding by cutting of flanges / valves / headers at all depth in all type of soil etc. Venting of N2 / gas / gas mixture as required purging of N2 Gas (if required), rebevelling as required, radiography and other NDT examination, joint coating as per specification.Contractor shall supply of all consumables, manpower, machinaries, materials, N2 gas etc. and carry out all works as per the provisions of Contract document and instructions of Engineer-in-charge. | Item86
87 | For 12" NB | Item87 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
88 | PRE-COMMISSIONING AND ASSISTANCE IN COMMISSIONING OF PIPELINE SYSTEM Swabbing, drying, purging with nitrogen of the complete pipeline network and the associated facilities being installed to the specified acceptance criteria, carrying out pre-commissioning works, providing assistance during the complete duration of commissioning operations for entire pipeline network system including supply of all equipment, man-power, consumables (including pigs & nitrogen required for purging with maintaining nitrogen column of mininum 10% of pipeline geometric volume) materials for all temporary works and performing all associated works, complete as per the relevant specifications, other provisions of Contract document and instructions of Engineer-in-charge. | Item88
89 | For 12" NB Pipeline | Item89 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
90 | IDLE TIME PRESERVATION OF PIPELINE Preservation of complete pipeline and associated facilities forming part of the pipeline as per Bid document and its maintenance including supply of all consumables, all equipment, manpower, etc. complete as per the requirements of specifications, other provisions of Contract document and instructions of Engineer-in-charge. Note : Owner reserves the right to exercise either or none of the rates below. | Item90
91 | By filling and pressurizing with nitrogen to a pressure of 2 bar(g) for a period of 3 months. | Item91 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
92 | For 12" NB Pipeline | Item92 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
93 | For every additional period of one month or part thereof | Item93 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
94 | For 12" NB Pipeline | Item94 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
95 | RCC VALVE PITS All civil works including supply of all materials, excavation of pit, piping supports including all PCC and RCC works for valves pits including pedestals with insert plates as required sealing of pipe at valve pits, providing cover etc. and finishing , clean-up and restoration of site, filling and grading of area around valve station for avoiding any local flooding of area, as per typical drawing and specification enclosed and instructions of Engineer-in-charge. In this item, instead of Brick Work, RCC will be done | Item95 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
96 | Valve Pit of Size 2m x 2m | Item96 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
97 | SUPPLY OF ASSORTED PIPE, FITTINGS AND FLANGES Complete works of supply of pipes, flanges & fittings for aboveground & underground installation including all taxes, duties, transportation and inspection charges but not limited to, the following items in accordance with PMS (piping material specification), relevant specifications & drawings indicated in job specification under SCC (technical) and instructions of Engineer-in-charge and as per all provisions of the CONTRACT DOCUMENT. - Handling including lifting, transportation from Contractor Stores to CONTRACTOR's workshop for fabrication and/ or to work site for field fabrication and erection for all piping items supplied by Contractor. | Item97
98 | Carbon Steel Pipe (A 106, Seamless B-36.10/ API X 52 ) | Item98
99 | Size Rating/ Schedule | Item99 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
100 | 2" NB, BE Sch. 80 | Item100 | 55 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
101 | 1" NB, PE Sch. 80 | Item101 | 38 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
102 | ¾" NB, PE Sch. 160 | Item102 | 36 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
103 | Flanges | Item103
104 | Weld Neck (B-16.5, 300# A105,125 AARH, Serrated finish) | Item104
105 | Size Rating/ Schedule | Item105 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
106 | 2" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item106 | 10 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
107 | Blind Flanges (B-16.5, 300# A105,125 AARH Serrated) | Item107
108 | Size | Item108
109 | 2" NB, RF | Item109 | 10 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
110 | Elbow (Seamless) | Item110 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
111 | 90° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item111
112 | Size Rating/ Schedule | Item112
113 | 12" NB 300# | Item113 | 24 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
114 | 45° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item114 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
115 | Size Rating/ Schedule | Item115
116 | 12" NB 300# | Item116 | 24 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
117 | 90° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item117 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
118 | Size Rating/ Schedule | Item118
119 | 12" NB 300# | Item119 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
120 | 45° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item120
121 | Size Rating/ Schedule | Item121
122 | 12" NB 300# | Item122 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
123 | 22½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D) Min Thickness 6.4mm | Item123 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
124 | Size Rating/ Schedule | Item124
125 | 12" NB Sch. Std. | Item125 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
126 | 11½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D), Min Thickness 6.4mm | Item126
127 | Size Rating/ Schedule | Item127
128 | 12" NB 300# | Item128 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
129 | Tees (Seamless) | Item129
130 | Equal Tee (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item130
131 | Size Rating/ Schedule | Item131
132 | 12" NB x 12" NB x 12" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item132 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
133 | 2" NB x 2" NB x 2" NB Sch. XS | Item133 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
134 | Weldolet and Sockolet | Item134
135 | Weldolet (MOC A105 & DIM. MSS SP 97) | Item135
136 | Size Rating/ Schedule | Item136
137 | 12" NB x 2" NB Sch. 80. | Item137 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
138 | Sockolet (MOC A105 & DIM. MSS SP 97) | Item138
139 | 12" NB x 3/4" NB #6000 | Item139 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
140 | Butt Weld Disc End Cap (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item140
141 | Size Rating/ Schedule | Item141
142 | 12" Sch. Std. | Item142 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
143 | Fabrication & Installation of Underground Valve Assembly | Item143 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
144 | 12"NB Isolation Valve/tap-off assembly as per Drg. No. MNGL/Plng./Steel/40 | Item144 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
145 | Note: | Item145 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
146 | For all the supply items mentioned above, procurement shall be made as per enclosed Data Sheets and respective technical specification, after due approval of Engineer-in-charge. | Item146
147 | The quantities mentioned above are tentative and quantities for above supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item147
148 | PLANT PIPING (ABOVEGROUND) Fabrication and testing of carbon steel piping and fittings, valves, IJ, including supply of all consumables, equipment, manpower, and other resources and execution of job as per instruction AIC/EIC.Transportation of all piping items from Owner's and/ or Contractor's storage point to work at site/ workshop as applicable, complete work of fabrication, erection, painting, testing of pipes, flanges and fittings and making ready for further Commissioning / Start-up of carbon steel piping of all sizes and ratings including supply of all consumables, equipment, manpower and other resources and execution of, but not limited to, as per all provisions of the CONTRACT DOCUMENT. | Item148 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
149 | Fabrication including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site, cutting, edge preparation, inclusive of grinding the edges of pipes, fittings, flanges, reducers etc. to match with the matching edges of uneven thickness, wherever required, fit-up, welding of pipes and fittings like elbows, tees, reducers, weldolets, sockolets, Valves, IJ etc. flanges, vent and drain point connection, Radiography and NDT of all joints etc, including providing stubin connections, fabricated fittings and reinforcement pads etc., as required. | Item149 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
150 | Erection of pipes of all types and thickness at all elevations, connecting with equipment nozzle, aligning, installation and carrying out connected activities for all types of valves, all online instruments and fittings of all sizes of elbow, reducers, tees, flanges, blind flanges, spectacle blind flanges, branch connection / tapping for pressure gauges, including installation of gaskets and bolts. | Item150 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
151 | Erection including prior cleaning, lifting, placing on pipe sleepers and supports, overhead on racks, skids and at all elevations including installation and carrying out connected activities for all types of valves including supply and fixing of gaskets, studs/ bolts, nuts wherever required for all sizes, levelling, aligning, joining of flanges, blind flanges, connecting with equipment, nozzles, strainers, tie-in with existing piping/facilities, etc. tapping for inline instruments like pressure gauges, thermowells, sample connection, etc. | Item151
152 | Hydro testing of the piping job shall be conducted at pressure mentioned in specification for a period of 4 hours by using de-mineralised water, to check its strength. No visible leakages shall be detected during the test. Testing shall be conducted as per tender specification. | Item152
153 | Preparation of final bill of material based on piping GADs. | Item153
154 | Preparation of isometric and fabrication drawings. | Item154
155 | Carrying out Non-destructive testing as required | Item155
156 | Painting of entire system (including aboveground all pipes fittings, flanges and accessories) as per specifications suitable for highly corrosive area environment including supply of approved paints and primers, application of primer and paints, indentification lettering/ numbering, colour coding, etc. as specified including rub down & touch up of shop primer or scrapping of shop primer wherever required by COMPANY and providing scaffolding for all heights etc. | Item156
157 | Cleaning and flushing by water/ compressed air, testing of the systems including hydrostatic, pneumatic and any other type of testing as specified, draining, drying by compressed air/other methods approved by COMPANY. | Item157
158 | Precommissioning & making operational all piping system and equipments. | Item158 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
159 | Commissioning Contractor scope shall provide all necessary assistance in term of supply of man-power, equipment, tools and tackles required amount of nitrogen for purging of entire terminal piping system including equipments etc. to the company during commissioning activities. | Item159 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
160 | Completion of all such work in all respects as per scope of work and as per drawings, specifications and instructions of the COMPANY and keeping the system ready in all respects for further commissioning and start up. | Item160 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
161 | Hook-up works (with client/ consumer piping at battery limits): | Item161 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
162 | Complete Carbon Steel aboveground Piping Work with painting including all fittings, flanges and supply of all required gaskets, studs bolts & nuts etc. and Any other work and material required for the completion of the work and not covered above and desired by EIC shall be in the scope of contractor | Item162 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
163 | Carbon Steel Pipe (ASTM A 106, Seamless B-36.10 / API X 52) | Item163 | 150 | inch Dia |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
164 | 1) Pipe Specification and thickness may vary depending upon availability of pipe. No extra payment shall be made for this. 2) All butt welded fittings & flanges end shall generally match with connecting pipe wall thickness. However, in case of misalignment, Contractor shall have to do end preparation without any extra cost. 3) All o-lets less than 2" NB size, all sizes of coupling and nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under erection rate. | Item164 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
165 | Aboveground installation of Insulating Joint & Valves etc. Handling including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site and installation of all types of valves, insulating joint including assembly of valve accessories, (if any) by bolting, threading or welding, supply and insertion of gaskets, nuts & bolts, nipples, etc. at all elevations of pipe sleepers, supports or overhead on racks, equipments nozzle, skid & painting etc. supply of all consumables, manpower, equipment, etc. for completion of all works as per scope of work and as per drawings, specifications and instructions of Engineer-in-charge including servicing/ cleaning of valve wherever requried. | Item165 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
166 | 12" NB, 300# - Insulating Joints | Item166 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
167 | STRUCTURAL WORKS | Item167 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
168 | Supply of erection of single leaf mild steel gate 2.5m high with mesh upto 2m height and barbed wire fencing and 2m wide complete in all respect including painting as per TS on all MS items, all works as per specification and drawings excluding foundations and RCC beams. | Item168 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
169 | Supply of all materials, fabrication and erection of chain link fencing 2.5m high with mesh up to 2m height and barbed wire fenching complete in all respects including painting as per TS on all MS items, all works as per specification and drawings excluding foundation and RCC beams. | Item169 | 150 | RM |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
170 | Pipe Supports & Other Structures | Item170 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
171 | Supply, fabrication and erection of all types of pipe supports like clamps, saddle, guide stops, cradles, turn buckles, anchors, T-posts; stockade/ trestle and pipe bridge for overhead piping; frames for canopy, approach ladders and platforms, crossover, cable tray supports, etc. including painting suitable for highly corrosive area as per specification labour and supervision & complete work as per drawings, specifications and instruction of Engineerqw-incharge. (Bolts, nuts, washers, U-clamps etc. for supporting shall be supplied by the Contractor within the rates quoted. These items will not be measured and paid seperately). The work is to be completed in all respect as per scope of work and specification. | Item171 | 200 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
172 | Notes: | Item172 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
173 | The quantities indicated are estimated values and hence are approximate. Final payment will be made based on actual quantities to be certified by the Purchaser. | Item173
174 | The cost of MS bolts (permanent and service(, washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants etc., as required for the work shall be deemed to be included in the quoted rates. | Item174 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
175 | All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accrodance with time schedule, are deemed be included in the quoted rates. | Item175
176 | CIVIL WORKS | Item176
177 | Site Grading Excavation in earth and filling to the grades and levels shown in the approved drawings in all kinds of conditions including for Road embarkments, using approved quality good earth from designated borrow area, for all heights and depths including clearing and stripping (min. 150mm) of the area marked for filling, taking spot levels, consolidating the exposed natural soil surface, excavating the earth from borrow area loading, transporting & unloading, spreading in layers not exceeding 150mm thickness, breaking clods, watering (if reqd.), ramming and compacting by manual/ mechanical means to give minimum 92% of modified Proctor's density of earth, testing & dressing including disposal of all unserviceable material all complete as per specifications and directions of Engineer-in-charge. | Item177 | 150 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
178 | (Rate to include cost of all labour, tools, tackles, equipment, hire charges, cost of borrow earth by way of royalties, right of way, cess etc., as applicable with all bye works and sundry works). | Item178
179 | Plain Cement Concrete Supplying and laying plain cement concrete (including shuttering of required) in all types of concrete works including levelling courses below foundation, substructure, superstrcuture, chambers, cable tranch, under floors and any other locations, at all leveies as per drawings, specifications and directions of the Engineer-in-charge. | Item179
180 | PCC 1:2:4 1 Cement : 2 Coarse sand : 4 stone aggregate 20mm nominal size. | Item180 | 500 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
181 | Reinforced Cement Concrete Providing and laying reinforced cement of grade M-20 with 20mm and down grade crushed stone aggregate in all types of structures like foundations, pedestals, pedestal bases, pipe supports, sleepers cable trench inlcuding constrcution joints, bitumen painting on surface in contact with soil, providing and fixing reinforcing steel, shuttering, inserts, finishes etc. at all depths and heights complete as per drawings, specifications and direction of the Engineer-incharge. | Item181 | 400 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
182 | Rate to include cost of all labour, tools, tackles, equipment, hire charges, supply of all maerials such as minimum 43 grade cement including sulphate resistant cement for substructures, R/F steel, Inserts, bolts, conduits, bitumen, other minor constrcution materials, shuttering, stanging, earthwork in excavation and backfilling using serviceable earth in all conditions, shorting bailing and pumping out water, testing of concrete, curing etc. with all bye works and syndry works. | Item182
183 | TEMPORARY CATHODIC PROTECTION SYSTEM | Item183
184 | Design, detailed engineering, supply, installation, testing and commissioning of the temporary Cathodic protection system using Mg/ Zn galvanic anodes to protect the external surface of 3 LPE coated entire 5.5 km (approx.) long steel pipeline network against corrosion for design life of minimum 1 year or till commissioning of PCP system whichever is later as per standard specification No. MNGL/Steel/TS/15 for temporary cathodic protection system. Scope shall also include but not limited to the following for completion of jobs: | Item184 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
185 | Measurement of soil resistivity along the right of way of the main pipeline route as per specification for design & installation of anodes. | Item185
186 | Collection of additional data related to cathodic protection along the right of way of pipeline as per specifications. | Item186 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
187 | Supply, installation, testing & commissioning of one set of spark gap arrestor with 2 plate Zinc grounding cell of 20 kg net weight each across each insulating joint as per specification. | Item187
188 | Supply, installation, testing & commissioning one set of polarisation cell with zinc anode at all high tension (66KV or higher) electrical power transmission line/Equipment crossing or running parallel to the pipeline for grounding purpose as per specification. The rating shall depend upon anticipated fault current & ground bed resistance at the location of installation. However, the rating of polarisation cell (krick) shall not be less than 5 KA & number of 20 kg net weight zinc anode shall not be less than two. | Item188
189 | Supply & installation of Zinc Ribbon Anodes at 4-8 O’Clock position in the interval of 2 metre (max.) on carrier pipes at all cased crossings i.e. railways/ roads etc. | Item189 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
190 | Monitoring of the protection system for 6 months. | Item190
191 | All civil/ structural works related to TCP system including supply of bricks, cement & steel etc. required for completion of the system. | Item191 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
192 | For 12" | Item192 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
193 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item193 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
194 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item194 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
195 | FIELD INSTRUMENTATION | Item195 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
196 | PRESSURE INSTRUMENTS | Item196
197 | Supply , Installation of Pressure Gagues and their accessories inclusive of supply of necessary piping materials and tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/ manifolds & hydraulic testing (exclusive of calibration of instruments) as per installation standard attached elsewhere in Tender Document and Supply as per Data Sheet No.MEC/23K8/05/E5/I/001/DS-PG. Give breakup of supply and Installation rate. | Item197 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
198 | CALIBRATION | Item198
199 | Calibration of the instruments listed below including removal of instruments from pre-installed locations like panels, enclosure racks, fields etc. and refixing them back in respective/ required places, providing equipments, necessary test jigs, instrument air and all consumables. Calibration reports shall be prepared and to be submitted to the Purchaser/ Consultant. | Item199
200 | Pressure Gauges | Item200 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
201 | Note: | Item201 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
202 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item202 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
203 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item203 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
204 | PIPING WORKS FOR SECTIONALISING VALVE STATION-CUM-TAP-OFF POINT All works for fabriaction and installation of all piping above ground at all elevations and below ground at all depth for Sectionalising Valve Station alongwith preparation of construction drawings duly approved by EIC, in all type of terrains and soils including transportation and handling of all Owner supplied materials i.e. extended stem butt welded sectionalising gas actuated ball valve, other types of valves, line pipes for mainline, 4" NB pipe for all branch line including ventlines from Owner's designated place(s) of issue to work site. | Item204 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
205 | Contractor shall supply all required size & type of piping material like pipes, fittings & flanges etc. as per PMS alongwith 2" NB pipe for all branch line & vent line (wherever required) including supply of all consumables, manpower, machinaries, materials etc. and carrying out all mechanical works of underground and above ground piping including fabrication, welding, nondestructive testing of welds, weld repairs/ retesting, cleaning/ flushing, pre-hydrotesting & hydrostatic testing, dewatering, functional testing, cutting of mainline and bevelling (if required) | Item205
206 | assembly, including radiography of tie-in joints, corrosion, coating and external painting as required, installation of instruments like pressure/ temperature instruments/ gauges alongwith complete SS Tubing works including supply of SS Tube and thier accessories etc., as required, obtaining all statutory clearances, approvals and permissions for the works (wherever required), making of valve pit (for detail refer relevant drawings) for SV Stationscum- tap-off points enclosed with tender filled with sand, excavation and filling in all types of soils including soft/ hard rock for installation of piping/ pipe supports providing pipe supports, area fencing and gate including all associated civil and structural works; painting, finishing, clean-up and restoration of site; preparation of as-built drawings, documents and project records and performing all works as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge. In this item, instead of Brick Work RCC will be done | Item206 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
207 | Type - I SV Station on 12" Pipeline | Item207 | 1 | Lumpsum for each |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
208 | Note: i) Work under above items are exclusive of all works associated with main pipeline covered under Item No. 1.0 above. ii) All civil/ structural works including area fencing and gate, valve pits except for piping support will be paid separately as per unit rate provided elsewhere in the SOR. iii) All coupling, nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under above item rate. | Item208 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
209 | Details of Major Road Crossing (Canal/SH/DR/NHAI): Supply, Installation & Insertion of pipeline across Canal / State Highways as per SCC and technical specifications | Item209 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
210 | Supply & Installation of 24" NB x 6.4mm Wall thk. Casing pipe for Line Pipe 12"NB(6.4 mm thk API 5L Gr X52) by Jacking Boring . Including Insertion of 12" dia Carrier pipeline in 24" dia casing pipe and connectivity with existing pipeline at both end of National Highways/State Highways/ Railway as per SCC and technical specifications -Supply of Casing Pipe Supply of following casing pipe including handling, loading, transportation & unloading etc. to contractor's own stock yard / worksite(s). -After Completion of insertion of carrier pipe with Connectivity at both end including all works as per the scope of work -Post Hydro testing & Commissioning , Submission of as-built drawing, Submission of Documents - The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. | Item210 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
211 | Note: (i) Crossing width may vary as per site condition. Tenderer are advised to visit site for actual assessment of extent of crossing. Actual length of Boring shall be as per design calculations so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. (ii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by Boring method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item211 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
212 | (iii) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossings at different locations. | Item212 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
213 | (iv) Actual length & cover from top of casing pipe string may vary depending upon site conditions, approved drawings, specification etc. and / or as decided by concerned Authority / Engineer-in-charge. (vi) No Extra Payment for supply & installation of Zinc ribbon to be provided to Carrier pipe & Zinc Anode is to be provided to Casing pipe and its design included in above item | Item213 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
214 | Supply and installation of 24'' casing pipe,Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insertion of carrier pipe in casing pipe after above ground pretesting at specified test pressure and installation of casing insulators & Zinc ribbon anode as per specification/ drawings. Installation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed (Any type of soil) | Item214 | 120 | Mtrs |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
Total in Figures | [51 empty] | 0 | 0 | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## BoQ15 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR | [49 empty] | 1
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Maharastra Natural Gas Ltd.,Pune
Name of Work: TENDER FOR LAYING & CONSTRUCTION OF 12” NB X 6 KM , 6" NB X 0.2 KM & 4" NB X 1.5 KM U/G STEEL PIPELINE NETWORK & ASSOCIATED WORKS FROM NEAR NYARA PUMP, KHARI ARDA TO NEAR SBI ATM AT DEGAON PHATA(Section No-15)
Tender No: MNGL/CP/2024-25/109
Do you want to quote for this sheet ? |  |  | Yes
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE / SCHEDULE OF RATES (SOR) (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Rate inclusive of all taxes and duties except Goods & Service Tax (Rs.) | Per Unit Goods & Service Tax (GST) In % (To be entered by the Bidder) | GST in Rs. | Unit rate inclusive of all taxes & duties including GST (Rs.) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | CARBON STEEL PIPES | Item1
2 | PIPELINE LAYING / INSTALLATION in all type of surface (Normal/built-up surface) "Receiving and taking over" as defined in the specifications, handing, loading, transportation and unloading of Owner supplied 3-Layer PE coated linepipes from Owner's designated stack-yard to Contractor's stock yard/workshop/work-site including preliminary activities, preparation of drawings, wherever required for crossing etc. including handling, stacking, stringing on the pipeline Right-of-Use/ pipeline route alignment, carrying out inspection of company supplied materials including linepipes at the time of taking over, laying/ installation of coated linepipes, associated burried valves, barred tees, insulating joints, flanges & fittings of all sizes, thickness & ANSI class rating and accessories as per specification wherever required depending on site condition including execution of all works, "taking over", handling , including loading and unloading, transportation of Owner supplied materials other than linepipe from Owner's designated place (s) of issue to work site, | Item2
3 | additional lands required for Contractor's storage, fabrication, access for construction, procurement and supply of all materials (except Owner supplied materials), consumables, equipment, labour and other inputs, carrying out all temporary, ancillary, auxiliary works, aquistion of ROU/ROW for laying of pipeline from HDD Exit and entry point to Tie in Point of existing Pipeline/ ROU, ready for commissioning of pipeline as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge, including but not limited to carrying out the following works: | Item3
4 | Surveying of route and detours required at the time of execution including marking the same in topographical sheet, preparation of construction drawings showing survey details, and submit same to Owner for review / approval. | Item4
5 | Staking and installation of construction markers, clearing, fencing, grubbing, cutting of trees, full filling all the requirements of various statutory/ environment authorities to the entire satisfaction of concerned authorities, grading of work area. Shifting of all obstruction within the ROU/ Pipeline route alignment viz. electrical lines/ poles, telephone line / poles, etc. coordination with concerned authorities and obtain permissions from these authorities. | Item5
6 | Trenching to all depths by excavation in all types of soils including soft/ hard rock and different type of pavement / footpath / roads etc. including rock breaking, chiselling or otherwise cutting etc. as required and storing excavated soil, reusable materials at designated area as directed by Engineer in charge and to a width to accommodate the Steel pipeline and MDPE as per the relevant standard/ specification etc. [The minimum depth of the top of pipeline shall be 1.2m measured from top of pipeline coating to the top of undisturbed surface of the soil or as per SCC/ OISD - 141 / 226, whichever is higher]. Dewater of trenches if required as per site condition. | Item6
7 | Carrying out repairs of pipe defects/ replacement in case of irreparable defects and repairs of defects of pipe coating not attributable to Owner including defects/ damages occurring during transportation / handling. | Item7
8 | Stringing of line pipes along pipeline trench / ROU on straw / sand / soft soil bags including supply of bags and its filling materials. | Item8
9 | Checking, cleaning, aligning, bending, cutting and bevelling (as required) of pipes for welding and field adjustments including pipe fittings, welding, carrying out non-destructive testing of welds as required including 100% radiography by X-ray and providing all requisite equipment, labour, supervision, materials, films, consumables, all facilities and personnel to process, develop, examine and interpret radiographs and other tests as required, carrying out repairs of weld joints found defective by Engineer-in-Charge, carrying out re-radiography and other tests as required on repaired joints. | Item9
10 | Carrying out installation of carrier line pipe at all minor crossing viz. carttrack, pathway, water bodies etc. at designated depth by open cut (except at crossing by HDD method). | Item10
11 | Carrying out installation of carrier line pipe in the casing pipe at cased crossing (excluding installation of casing pipes which is covered separately). | Item11
12 | Coating of field weld joints, long radius bends (R=3D), elbows, buried fittings and valves etc. including supply of coating materials etc. (i.e. heat shrinkable sleeves and high build epoxy etc.) as per PJS & Technical Specification compatible with 3 layer PE coating material of the line pipe. | Item12
13 | Counting the number and type of trees cut in presence of DFO/concerned authorities and keeping record thereof, stacking and handing over of all cut tress. | Item13
14 | Installation / lowering the pipeline in trench to required depth as per PJS, Techanical Specification & drawings, supply & placement of 1.0mm thk. HDPE Yellow colour warning mat,RCC tiles (300 mm width x 50 mm thick) over the pipeline & MDPE Pipe in same trench along the complete route as per standard drawings, data sheets & technical specifications, padding around pipeline as per Standard Drg. no. MNGL/Plng./Steel/03 with suitable soil duly approved by EIC including supply of padding material, backfilling and its compaction to the satisfaction of concerned authorities with excavated earth / borrowed select soil including supply of borrowed select soil duly approved by EIC before backfilling and make ready for restoration to be done by Onwer / concerned authorities. | Item14
15 | Supply and installation of slope breakers, wherever required or, as directed by Onwer / Engineer–in–charge. | Item15
16 | Crossing the all-foreign pipeline / HT line / cable / any other utilities etc. with necessary concrete / HDPE sheet protection including coordination with all agencies and obtaining NOC | Item16
17 | Supply and installation of bank protection alongwith backfill materials duly approved by EIC for pipeline trench and banks falls under minor water body crossing as per technical specification & Std. Drg. No. MNGL/Plng./Steel/28, wherever required or, as directed by Onwer / EIC. | Item17
18 | Training and diversions of streams in steep slope area, wherever required. | Item18
19 | Carrying out air cleaning, pigging, flushing, cleaning and hydrostatic testing of complete pipeline with required quantity of corrosion inhibitor including pre-testing of designated sections complete as per specification and approved by Engineer–in–charge to specified pressures indicated elsewhere and duration after stabilization as per specification, providing all equipment, pumps, fittings, instruments, dead weight tester, pressure recorder, thermocouples etc., and services, supervision, labour, consumables, water including supply of corrosion inhibitor, air, etc. as required, locating of leaks and rectification of defect attributable to Contractor (rectification of defects in linepipe material not attributable to contractor shall be paid separately as per other item of schedule of rate), re-testing after rectification, dewatering after successful completion of hydrotesting of entire section and as per specification | Item19
20 | All tieing-in, including the tie-in(s) of the pipeline with the adjacent sections of pipeline including cutting of test header, rebevelling as required, radiography and other NDT examination, joint coating as per specification. | Item20
21 | Final clean-up of right-of-use or area disturbed by contractor during their construction activities for laying of pipeline works and disposal of debris and surplus material to designated disposal areas and backfilling of trench and compaction of the same as per satisfaction of Owner and / Or as directed by Engineer–in–charge. | Item21
22 | Installation of all burried valves (except extended stem valves) inside the valve pit and making provision to operate the valve. | Item22
23 | Preparation of as-built drawings, pipe-books (1 set of tracing on polyester film and 6 sets of as-built drawings and 1 soft copy and 6 hard copies of pipe book) All the works shall be executed in accordance with the provision of contract including carrying out all temporary/ ancillary/ auxiliary works required for the performance of the works and all other acts, deeds, matters and things necessary to make the pipeline ready for precommissioning activities. | Item23
24 | Raking up of hard surface of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. Payment for cutting of hard rock, if any, is covered unders SOR no. 96 | Item24
25 | Specified dia Thk (mm) Material Coating Type Length of each pipe (mm) NB | Item25
26 | 305 (approx.) 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item26 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
27 | 150 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item27 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
28 | 100 6.4 API X-52 3 Layer PE Coating (Externally) Double random (approx. 11.5 m to 12.5 m) | Item28 | 1040 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
29 | Note: This item shall be applicable for the underground steel grid main pipeline & branch pipeline, barred tees, insulating joints, bends, flanges & fittings, accessories etc. (i.e. including arrangement for making provision for tap-off on proposed steel grid main pipeline) and aboveground approach pipeline upto Insulating Joint (excluding installation of aboveground insulating joint) for various stations. | Item29
30 | Items except above are covered separately. The lengths of pipelines are tentative. | Item30
31 | Permission Liasioning /Follow-up | Item31
32 | Liasioning & follow up for Permission with all the concerned authorities & boards viz Railways, NH, PWD, MIDC, Local Municipal, Panchyat, Electricity, REC, RES, Sewage water, Drinking water, Forest, Social Forestry, Owners of OFC, Traffic, Law & Order, Fire Brigade, Private Land Owner etc. for entire pipeline length and associated terminals (like SVs, tap-offs) alongwith associated work as per tender. | Item32 | 7700 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
33 | Laying of RCC Tiles | Item33
34 | Providing single layer of RCC Tiles with supply of RCC Tiles to entire width of trench above Warning Mat placed in trench over the laid pipeline as per standard drawing, specification and instruction of Owner. (Rate to include cost of all labour, tools, tackles, equipment, hire charges & supply of all materials, etc.) | Item34
35 | For width of 12" pipeline trench | Item35 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
36 | For width of 6" pipeline trench | Item36 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
37 | For width of 4" pipeline trench | Item37 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
38 | Barricading to comply with HSSE | Item38
39 | Steel barricading of the trenches Cautionary Sign Boards and lighting arrangement shall be provided as per attched drawing no.MNGL/Plng./steel/04. The rates include barricading of trenches along with sign boards, lighting etc. and maintain the same till the back filling of the trench. Rates will be payable per metre of BARRICADING PROVIDED. If proper barricading is not provided, MNGL will barricade the trenches at the risks and costs of the CONTRACTOR and will levy penalty of twice the rate per unit for the relevant section of the pipeline apart from other actions as per contract. | Item39 | 7700 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
40 | RESTORATION OF ROADS Restoration of asphalt / concrete / red stone roads / pavement/Footpath/Paver block including compaction of soil, to original condition as per requirement and to the entire satisfaction of EIC and / or concerned Owners having jurisdiction for following thickness. | Item40
41 | Restoration of Asphalt road upto 10 cm thickness | Item41 | 800 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
42 | Restoration of Asphalt road beyond 10 cm upto 20 cm thickness | Item42 | 150 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
43 | Restoration of Concrete road upto 10 cm thickness | Item43 | 800 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
44 | Restoration of red stone road / footpath / pavement/ Paverblock upto 4 cm thickness | Item44 | 900 | Sq. metre |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
45 | BORROWED SELECT SOIL FOR BACKFILLING Additional work over and above item 1.0 for supply of specified and approved quality of borrowed soft graded soil / sand in place of available excavated material and / or other suitable soil as per applicable standards / specifications, including backfilling of excavated trench for specified length after laying and padding of pipeline, including transportation of such special backfill material over all distances, complete. | Item45 | 900 | m3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
46 | CROSSING OF STEEL PIPELINE BY OPEN CUT | Item46
47 | Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insatllation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed. | Item47
48 | Road Crossing By Open Cut Method Road Crossings at various locations by Open cut Method along with laying of MDPE upto 180 mm Dia if necessary as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item48
49 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item49 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
50 | Line pipe detail 6" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item50 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
51 | Line pipe detail 4" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item51 | 60 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
52 | Water body Crossing By Open Cut Method water/ canal/ nallah/ drain/ channel Crossings at various locations by Open cut Method along with laying of MDPE upto 180 mm Dia if necessary as decided by EIC at site as per concerned authority requirement.Depth of Line at crossing shall be as mentioned in Tender. | Item52
53 | Line pipe detail 12" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item53 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
54 | Line pipe detail 6" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item54 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
55 | Line pipe detail 4" NB, 6.4 mm thk API X-52 pipe, C.S. by open cut method along with laying of MDPE upto 180 mm Dia if necessary | Item55 | 50 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
56 | Note: Laying of the pipeline by the approved method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item56
57 | Backfilling of the Road/water/ canal/ nallah/ drain/ channel Crossings/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority. | Item57
58 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item58
59 | CROSSINGS/LAYING ALONG THE ROAD BY HDD METHOD | Item59
60 | Complete work of the any crossing (between the limits are defined as approved drawings) by HDD method including "Receiving and taking over" owner supplied three layer PE coated line pipes from Owner's designated place to issue/ dump site(s) and transportation to Contractor's stock yard/ work shop/ work site including all handling loading, unloading, aligning etc. supply of all Contractor supplied material, manpower, equipment, other resources and aquiring the required land for storage, fabrication inclduing string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type Heat Shrink Sleeve and repair of pipeline coating with special repair patch materials as per specification,pre-testing etc. of complete string made for crossing access for Contractor etc and execution of, but not limited to, following works in accordance with specifications scope of work and instructions of Engineer-in-charge and as per all provision of Contract Document. | Item60
61 | Pre-construction surveys based on site visit, collection of historical data from irrigation/ concerned department including design & calculation and detail engineering and making of crossing drawing for getting their approval from concerned Authority/ Engineer-in-charge, getting work permit/ NOC for water crossings/ road crossings as well as utility crossings (if any) encountered during crossing prior to start the execution of work. | Item61
62 | Directional drilling to required depth from top of road including maintenance of drill hole in all types of strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) at all depth to accommodate the pipeline at all conditions encountered during rail/ road crossing by approved HDD methods for providing minimum cover specified in code/ specification or the actual depth as decided by concerned authority, whichever is more. | Item62
63 | In case of water crossing, drilling to the required depth on the banks and bed including maintenance of drill hole in all types of soil strata ( other than hard rock,crossing by HDD in Hard rock is covered seperately) all depth to accommodate the pipeline a by HDD methods for providing with minimum cover over top of the pipe at all point across the maximum possible width of water bed (as per drawing) either 1.5 mtrs. below the predicted scour profile expected during the life time of the pipeline or 2.5 mtrs. below the available lowest firm bed (if scour profile/ depth not available) of the water crossing by ascertaining bed level upto 50 mtrs. both the side from crossing location or the actual depth as decided by concerned Authority/ Engineer-in-charge whichever is more. | Item63
64 | Laying of the pipeline by the approved HDD method across the crossing including, strings preparation of pipes, welding, testing, radiography, welding repair and retest, coating of field joints with special type Dirax Heat Shrink Sleeve or equivalent and repair of pipeline coating with special PERP-80 repair patch or equivalent material as per specification, pre-hydrotest of complete strings made for crossing etc. | Item64
65 | Backfilling of the ditch/ trench including restoration and clean-up of area etc. to the satisfaction of Engineer-in-charge/ Concerned Authority and all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specification, approved drawings, calculations, methods and to the satisfaction of Engineer-in-charge and/or as directed by concerned Authority. | Item65
66 | Post installation hydrotest dewatering and tie-in with pipeline at either side of crossing/banks etc. | Item66
67 | All other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) required as per specifications, codes, approved drawings, calculations, methods and as directed by Engineer-in-charge. | Item67
68 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 (along with laying of 4'' Steel Pipe for MDPE if necessary) by HDD Method . | Item68 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
69 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 150 mm NB x 6.4 mm thk. of API X-52 (along with laying of 4" Steel Pipe for MDPE if necessary) by HDD Method. | Item69 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
70 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 100 mm NB x 6.4 mm thk. of API X-52 (along with laying of 4" Steel Pipe for MDPE if necessary) by HDD Method. | Item70 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
71 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item71 | 180 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
72 | Laying along the Road by carrier pipeline of size 150 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item72 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
73 | Laying along the Road by carrier pipeline of size 100 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item73 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
74 | Installation of carrier pipes by rock drilling for Road/water/Canal/ nallah/ drain/ channel/along the road, or wherever required in all types of hard rock. It includes survey of the underground utilities, submission of profile for approval, execution of the work as per the standard procedure, including , excavation of the pits, insertion/pulling of the carrier pipe, removal of malba, subsequent backfilling and restoration of the facility crossed as per original condition, including supply of all other materials, equipment, consumables, manpower etc including string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type of Heat Shrink Sleeve (Direx) and repair of pipeline coating with special repair patch materials as per Specification, pre-testing etc. of complete string made for crossing/ laying access for Contractor etc. and execution of, but not limited to, following works in accordance with specifications and instruction of Engineer-in-Charge and as per all provision of Contract Document. Balance activities as defined in SOR Item of open trench. Note:The length of HDD mentioned is tentative and may vary to the considerable extent depending upon requirements as per site conditions. The length mentioned in SOR is indicative for all the crossing to be done by HDD, numbers and locations shall be decided by Engineer-in-Charge depending upon site condition. Payment for the length of final tie-in carrier pipeline string with mainline laid by HDD are inclusive in this above item rate. No separate payment shall be made under other clauses mentioned elsewhere. Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item74
75 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 305 (approx.) mm NB x 6.4 mm thk. of API X-52 (along with laying of 4'' Steel Pipe for MDPE if necessary) by HDD Method . | Item75 | 180 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
76 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 150 mm NB x 6.4 mm thk. of API X-52 (along with laying of 4" Steel Pipe for MDPE if necessary) by HDD Method. | Item76 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
77 | Crossing of nallah/ drain/ channel/River crossings by carrier pipeline of size 100 mm NB x 6.4 mm thk. of API X-52 (along with laying of 4" Steel Pipe for MDPE if necessary) by HDD Method. | Item77 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
78 | Laying along the Road by carrier pipeline of size 305 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item78 | 160 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
79 | Laying along the Road by carrier pipeline of size 150 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item79 | 20 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
80 | Laying along the Road by carrier pipeline of size 100 mm NB x 6.4 mm thk. of API X-52 by HDD Method | Item80 | 90 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
81 | Note: (i) Crossing width & Actual string length for HDD shall vary as per design calculations & site condition so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. | Item81
82 | (ii)Payment shall be based on the actual length (i.e. length between tie-in joints) of pipeline laid by HDD. Exact location of tie-in shall be approved by Owner/ Owner's representative. Above Rate for steel pipeline laying is inclusive of carrier pipe string preparation, Welding, NDT, Pretesting, Coating, Post Hydrotesting, Hydrotesting, Precommissioning & etc. | Item82
83 | (iii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by HDD method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item83
84 | (iv) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossing at different locations. | Item84
85 | (v) The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. | Item85
86 | Note: (i) Quantity mentioned under item nos. 48, 52 are indicative only for different location of roads/water/ canal/ nallah/ drain/ channel Crossings. (ii) Actual length & width of individual crossing and cover from top of casing pipe/ carrier pipe string may vary depending upon site condition, approved crossing drawings, specifications etc. and / or as decided by Engineer-in-charge/ Concerned Authority. | Item86
87 | (iii) Payment for supply & installation of Zinc ribbon anode and its design excluded from above item and covered elsewhere in the SOR. (iv) Payment for the length carrier pipeline string inserted in casing pipe laid by Boring are covered separately and shall be paid under other clauses mentioned elesewhere in the SOR. | Item87
88 | Excavation beyond 1.5m depth in case of crossing of utilities/ drain/ culverts etc. through open cut upto the following depth (including restoration of the damaged area to its original condition and satisfaction of the Engineer-in-charge / concerned authorities) : - | Item88
89 | In all type of surface (Kachha/ built-up surface / Hard surface) of any type including metal, concrete, bituminous, tiled, brick lined soft rock which is breakable in pieces manually (without use of pneumatic machine) etc. All tiles/ slabs/ curb stones etc. removed during excavation shall be placed properly. The other activities are as per SOR 1.1. Payment for cutting of hard rock, if any, is covered unders SOR no. 96 | Item89
90 | Deeper than 1.5 m & upto 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item90 | 800 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
91 | Deeper than 2.5 m below existing level (for 305 (approx.) mm NB Pipeline) | Item91 | 300 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
92 | Deeper than 1.5 m & upto 2.5 m below existing level (for 150 (approx.) mm NB Pipeline) | Item92 | 40 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
93 | Deeper than 2.5 m below existing level (for 150 (approx.) mm NB Pipeline) | Item93 | 40 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
94 | Deeper than 1.5 m & upto 2.5 m below existing level (for 100 (approx.) mm NB Pipeline) | Item94 | 300 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
95 | Deeper than 2.5 m below existing level (for 100 (approx.) mm NB Pipeline) | Item95 | 80 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
96 | Excavation of hard rock | Item96
97 | Excavation of hard rock wherever hard rock of single piece exceeding 1.0 m in length removable by pneumatic chisel/ drill as per direction of EIC. | Item97 | 3800 | Cub. M |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
98 | REPAIR OF COATING DEFECTS (NOT ATTRIBUTED TO CONTRACTOR) | Item98
99 | Repair of Holiday in Coating (Noted and recorded at the time of "receiving and taking over") Supply of all coating repair materials as per requirements of specification to be compatible with line pipe coating material, supply of all consumables, utilities, equipments and all manpower required, pipe cleaning and surface preparation, repairing of coating defects (resulting in holiday) and testing including all handling, transportation, etc. for line pipes, performing all works necessary for the completion of the works stirctly in accordance with relevant specification and instructions of Engineer-In-Charge. This rate shall be applicable per sq. cm of the exposed steel area exposed steel area. | Item99 | 2200 | Sq. cm. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
100 | PERMANENT MARKERS Supply, fabrication and installation of all types of permanent markers along the route including all associated civil works such as excavation in all types of soil, construction in all types of soil, construction of pedestals and grouting with concrete, clearing, supply and application of approved colour and quality of primer and paint, stencil letter cutting for numbers, direction, change etc., restoration of area to original condition and performing all works as per drawing, specification and instruction of engineer-in-charge. | Item100
101 | Pipeline RCC boundary / route marker as per drawing | Item101 | 120 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
102 | Pipeline warning markers with post & foundations | Item102 | 40 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
103 | Pipeline direction marker with post & foundations | Item103 | 25 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
104 | Pipeline KM with post & foundations | Item104 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
105 | HOOK -UP | Item105
106 | Hook-up of proposed pipeline by welding of final tie-in-joint with any existing laid pipeline portion of river X-ing ,existing Tap-off & battery limit of section IV including Hook-up point of the existing pipeline to be made ready for welding by cutting of flanges / valves / headers at all depth in all type of soil etc. Venting of N2 / gas / gas mixture as required purging of N2 Gas (if required), rebevelling as required, radiography and other NDT examination, joint coating as per specification.Contractor shall supply of all consumables, manpower, machinaries, materials, N2 gas etc. and carry out all works as per the provisions of Contract document and instructions of Engineer-in-charge. | Item106
107 | For 12" NB | Item107 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
108 | For 6" NB | Item108 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
109 | For 4" NB | Item109 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
110 | PRE-COMMISSIONING AND ASSISTANCE IN COMMISSIONING OF PIPELINE SYSTEM Swabbing, drying, purging with nitrogen of the complete pipeline network and the associated facilities being installed to the specified acceptance criteria, carrying out pre-commissioning works, providing assistance during the complete duration of commissioning operations for entire pipeline network system including supply of all equipment, man-power, consumables (including pigs & nitrogen required for purging with maintaining nitrogen column of mininum 10% of pipeline geometric volume) materials for all temporary works and performing all associated works, complete as per the relevant specifications, other provisions of Contract document and instructions of Engineer-in-charge. | Item110
111 | For 12" NB Pipeline | Item111 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
112 | For 6" NB Pipeline | Item112 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
113 | For 4" NB Pipeline | Item113 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
114 | IDLE TIME PRESERVATION OF PIPELINE Preservation of complete pipeline and associated facilities forming part of the pipeline as per Bid document and its maintenance including supply of all consumables, all equipment, manpower, etc. complete as per the requirements of specifications, other provisions of Contract document and instructions of Engineer-in-charge. Note : Owner reserves the right to exercise either or none of the rates below. | Item114
115 | By filling and pressurizing with nitrogen to a pressure of 2 bar(g) for a period of 3 months. | Item115
116 | For 12" NB Pipeline | Item116 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
117 | For 6" NB Pipeline | Item117 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
118 | For 4" NB Pipeline | Item118 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
119 | For every additional period of one month or part thereof | Item119
120 | For 12" NB Pipeline | Item120 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
121 | For 6" NB Pipeline | Item121 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
122 | For 4" NB Pipeline | Item122 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
123 | RCC VALVE PITS All civil works including supply of all materials, excavation of pit, piping supports including all PCC and RCC works for valves pits including pedestals with insert plates as required sealing of pipe at valve pits, providing cover etc. and finishing , clean-up and restoration of site, filling and grading of area around valve station for avoiding any local flooding of area, as per typical drawing and specification enclosed and instructions of Engineer-in-charge. In this item, instead of Brick Work, RCC will be done | Item123
124 | Valve Pit of Size 2m x 2m | Item124 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
125 | Valve Pit of Size 1.5m x 1 m | Item125 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
126 | Valve Pit of Size 1 m x 1 m | Item126 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
127 | SUPPLY OF ASSORTED PIPE, FITTINGS AND FLANGES Complete works of supply of pipes, flanges & fittings for aboveground & underground installation including all taxes, duties, transportation and inspection charges but not limited to, the following items in accordance with PMS (piping material specification), relevant specifications & drawings indicated in job specification under SCC (technical) and instructions of Engineer-in-charge and as per all provisions of the CONTRACT DOCUMENT. - Handling including lifting, transportation from Contractor Stores to CONTRACTOR's workshop for fabrication and/ or to work site for field fabrication and erection for all piping items supplied by Contractor. | Item127
128 | Carbon Steel Pipe (A 106, Seamless B-36.10/ API X 52 ) | Item128
129 | Size Rating/ Schedule | Item129
130 | 2" NB, BE Sch. 80 | Item130 | 55 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
131 | 1" NB, PE Sch. 80 | Item131 | 38 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
132 | ¾" NB, PE Sch. 160 | Item132 | 36 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
133 | Flanges | Item133
134 | Weld Neck (B-16.5, 300# A105,125 AARH, Serrated finish) | Item134
135 | Size Rating/ Schedule | Item135
136 | 6" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item136 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
137 | 4" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item137 | 5 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
138 | 2" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item138 | 10 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
139 | 3/4" NB, RF End thickness to match with pipe wall thickness (Sch. 80) | Item139 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
140 | Blind Flanges (B-16.5, 300# A105,125 AARH Serrated) | Item140
141 | Size | Item141
142 | 6" NB, RF | Item142 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
143 | 4" NB, RF | Item143 | 5 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
144 | 2" NB, RF | Item144 | 10 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
145 | 3/4" NB, RF | Item145 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
146 | Elbow (Seamless) | Item146
147 | 90° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item147
148 | Size Rating/ Schedule | Item148
149 | 12" NB 300# | Item149 | 24 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
150 | 6" NB 300# | Item150 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
151 | 4" NB 300# | Item151 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
152 | 2" NB Sch. 80 | Item152 | 6 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
153 | 45° Elbow ( MOC MSS SP 75 WPHY 52 & DIM. ASME 16.9 R=1.5D ) Min Thickness 6.4mm | Item153
154 | Size Rating/ Schedule | Item154
155 | 12" NB 300# | Item155 | 24 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
156 | 6" NB 300# | Item156 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
157 | 4" NB 300# | Item157 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
158 | 2" NB Sch. 80 | Item158 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
159 | 90° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item159
160 | Size Rating/ Schedule | Item160
161 | 12" NB 300# | Item161 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
162 | 6" NB 300# | Item162 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
163 | 4" NB 300# | Item163 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
164 | 45° Elbow (MOC MSS SP 75 WPHY 52 R= 3D ) Min Thickness 6.4mm | Item164
165 | Size Rating/ Schedule | Item165
166 | 12" NB 300# | Item166 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
167 | 6" NB 300# | Item167 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
168 | 4" NB 300# | Item168 | 10 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
169 | 22½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D) Min Thickness 6.4mm | Item169
170 | Size Rating/ Schedule | Item170
171 | 12" NB Sch. Std. | Item171 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
172 | 6" NB End thickness to match with pipe wall thickness | Item172 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
173 | 11½° Elbow (MOC MSS SP 75 WPHY 52 R= 3D), Min Thickness 6.4mm | Item173
174 | Size Rating/ Schedule | Item174
175 | 12" NB 300# | Item175 | 18 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
176 | 6" NB 300# | Item176 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
177 | Tees (Seamless) | Item177
178 | Equal Tee (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item178
179 | Size Rating/ Schedule | Item179
180 | 12" NB x 12" NB x 12" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item180 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
181 | 6" NB x 6" NB x 6" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item181 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
182 | 4" NB x 4" NB x 4" NB Min. Thickness 6.4mm X min. Thickness 6.4mm | Item182 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
183 | 2" NB x 2" NB x 2" NB Sch. XS | Item183 | 8 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
184 | Unequal Tee (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item184
185 | Size Rating/ Schedule | Item185
186 | 12" NB x 12" NB x 6" NB Sch. Std. x Sch. Std. | Item186 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
187 | 12" NB x 12" NB x 4" NB Sch. Std. x Sch. Std. | Item187 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
188 | 4" NB x 4" NB x 2" NB Sch. 80 x Sch.80 | Item188 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
189 | 6" NB x 6" NB x 4" NB Sch. Std.x Sch. XS | Item189 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
190 | Reducer (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item190
191 | 12" NB x 6" NB Min Thickness 6.4mm | Item191 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
192 | 12" NB x 4" NB Min Thickness 6.4mm | Item192 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
193 | 6" NB X 4" NB Min Thickness 6.4mm | Item193 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
194 | 4" NB X 2" NB Min Thickness 6.4mm | Item194 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
195 | Weldolet and Sockolet | Item195
196 | Weldolet (MOC A105 & DIM. MSS SP 97) | Item196
197 | Size Rating/ Schedule | Item197
198 | 12" NB x 2" NB Sch. 80. | Item198 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
199 | 6" NB x 2" NB Sch.80 | Item199 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
200 | 4" NB x 2" NB Sch. 80 | Item200 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
201 | Sockolet (MOC A105 & DIM. MSS SP 97) | Item201
202 | 12" NB x 3/4" NB #6000 | Item202 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
203 | 6" NB x 3/4" NB #3000 | Item203 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
204 | 6" NB x 1" NB #3000 | Item204 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
205 | 4" NB x 3/4" NB #3000 | Item205 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
206 | Butt Weld Disc End Cap (MOC MSS SP 75 WPHY 52 & DIM. ASME B16.9) | Item206
207 | Size Rating/ Schedule | Item207
208 | 12" Sch. Std. | Item208 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
209 | 6" Sch. 40 | Item209 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
210 | 4" Sch. 80 | Item210 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
211 | Fabrication & Installation of Underground Valve Assembly | Item211
212 | 12"NB Isolation Valve/tap-off assembly as per Drg. No. MNGL/Plng./Steel/40 | Item212 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
213 | 6" NB Isolation Valve/tap-off assembly as per Drg. No.MNGL/Plng./Steel/40 | Item213 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
214 | 4" NB Isolation Valve/tap-off assembly as per Drg. No. MNGL/Plng./Steel/40 | Item214 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
215 | Note: | Item215
216 | For all the supply items mentioned above, procurement shall be made as per enclosed Data Sheets and respective technical specification, after due approval of Engineer-in-charge. | Item216
217 | The quantities mentioned above are tentative and quantities for above supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item217
218 | PLANT PIPING (ABOVEGROUND) Fabrication and testing of carbon steel piping and fittings, valves, IJ, including supply of all consumables, equipment, manpower, and other resources and execution of job as per instruction AIC/EIC.Transportation of all piping items from Owner's and/ or Contractor's storage point to work at site/ workshop as applicable, complete work of fabrication, erection, painting, testing of pipes, flanges and fittings and making ready for further Commissioning / Start-up of carbon steel piping of all sizes and ratings including supply of all consumables, equipment, manpower and other resources and execution of, but not limited to, as per all provisions of the CONTRACT DOCUMENT. | Item218
219 | Fabrication including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site, cutting, edge preparation, inclusive of grinding the edges of pipes, fittings, flanges, reducers etc. to match with the matching edges of uneven thickness, wherever required, fit-up, welding of pipes and fittings like elbows, tees, reducers, weldolets, sockolets, Valves, IJ etc. flanges, vent and drain point connection, Radiography and NDT of all joints etc, including providing stubin connections, fabricated fittings and reinforcement pads etc., as required. | Item219
220 | Erection of pipes of all types and thickness at all elevations, connecting with equipment nozzle, aligning, installation and carrying out connected activities for all types of valves, all online instruments and fittings of all sizes of elbow, reducers, tees, flanges, blind flanges, spectacle blind flanges, branch connection / tapping for pressure gauges, including installation of gaskets and bolts. | Item220
221 | Erection including prior cleaning, lifting, placing on pipe sleepers and supports, overhead on racks, skids and at all elevations including installation and carrying out connected activities for all types of valves including supply and fixing of gaskets, studs/ bolts, nuts wherever required for all sizes, levelling, aligning, joining of flanges, blind flanges, connecting with equipment, nozzles, strainers, tie-in with existing piping/facilities, etc. tapping for inline instruments like pressure gauges, thermowells, sample connection, etc. | Item221
222 | Hydro testing of the piping job shall be conducted at pressure mentioned in specification for a period of 4 hours by using de-mineralised water, to check its strength. No visible leakages shall be detected during the test. Testing shall be conducted as per tender specification. | Item222
223 | Preparation of final bill of material based on piping GADs. | Item223
224 | Preparation of isometric and fabrication drawings. | Item224
225 | Carrying out Non-destructive testing as required except items mentioned in sl. no. 286 of SOR. | Item225
226 | Painting of entire system (including aboveground all pipes fittings, flanges and accessories) as per specifications suitable for highly corrosive area environment including supply of approved paints and primers, application of primer and paints, indentification lettering/ numbering, colour coding, etc. as specified including rub down & touch up of shop primer or scrapping of shop primer wherever required by COMPANY and providing scaffolding for all heights etc. | Item226
227 | Cleaning and flushing by water/ compressed air, testing of the systems including hydrostatic, pneumatic and any other type of testing as specified, draining, drying by compressed air/other methods approved by COMPANY. | Item227
228 | Precommissioning & making operational all piping system and equipments. | Item228
229 | Commissioning Contractor scope shall provide all necessary assistance in term of supply of man-power, equipment, tools and tackles required amount of nitrogen for purging of entire terminal piping system including equipments etc. to the company during commissioning activities. | Item229
230 | Completion of all such work in all respects as per scope of work and as per drawings, specifications and instructions of the COMPANY and keeping the system ready in all respects for further commissioning and start up. | Item230
231 | Hook-up works (with client/ consumer piping at battery limits): | Item231
232 | Complete Carbon Steel aboveground Piping Work with painting including all fittings, flanges and supply of all required gaskets, studs bolts & nuts etc. and Any other work and material required for the completion of the work and not covered above and desired by EIC shall be in the scope of contractor | Item232
233 | Carbon Steel Pipe (ASTM A 106, Seamless B-36.10 / API X 52) | Item233 | 250 | inch Dia |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
234 | 1) Pipe Specification and thickness may vary depending upon availability of pipe. No extra payment shall be made for this. 2) All butt welded fittings & flanges end shall generally match with connecting pipe wall thickness. However, in case of misalignment, Contractor shall have to do end preparation without any extra cost. 3) All o-lets less than 2" NB size, all sizes of coupling and nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under erection rate. | Item234
235 | Aboveground installation of Insulating Joint & Valves etc. Handling including lifting and transportation from COMPANY's warehouse to CONTRACTOR'S Stores and/or work site and installation of all types of valves, insulating joint including assembly of valve accessories, (if any) by bolting, threading or welding, supply and insertion of gaskets, nuts & bolts, nipples, etc. at all elevations of pipe sleepers, supports or overhead on racks, equipments nozzle, skid & painting etc. supply of all consumables, manpower, equipment, etc. for completion of all works as per scope of work and as per drawings, specifications and instructions of Engineer-in-charge including servicing/ cleaning of valve wherever requried. | Item235
236 | Welded Valves (Full Bore/ Reduced Bore) Ball / Globe / Check Valve | Item236
237 | Size Rating/ Schedule | Item237
238 | 4" NB 300# | Item238 | 4 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
239 | 2" NB 300# | Item239 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
240 | Sockolet Welded Valve (Ball / Globe Valve) | Item240
241 | Size Rating/ Schedule | Item241
242 | 1" NB 800# | Item242 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
243 | ¾" NB 800# | Item243 | 3 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
244 | 12" NB, 300# - Insulating Joints | Item244 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
245 | 6" NB, 300# - Insulating Joints | Item245 | 1 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
246 | 4" NB, 300# - Insulating Joints | Item246 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
247 | STRUCTURAL WORKS | Item247
248 | Supply of erection of single leaf mild steel gate 2.5m high with mesh upto 2m height and barbed wire fencing and 2m wide complete in all respect including painting as per TS on all MS items, all works as per specification and drawings excluding foundations and RCC beams. | Item248 | 20 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
249 | Supply of all materials, fabrication and erection of chain link fencing 2.5m high with mesh up to 2m height and barbed wire fenching complete in all respects including painting as per TS on all MS items, all works as per specification and drawings excluding foundation and RCC beams. | Item249 | 150 | RM |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
250 | Pipe Supports & Other Structures | Item250
251 | Supply, fabrication and erection of all types of pipe supports like clamps, saddle, guide stops, cradles, turn buckles, anchors, T-posts; stockade/ trestle and pipe bridge for overhead piping; frames for canopy, approach ladders and platforms, crossover, cable tray supports, etc. including painting suitable for highly corrosive area as per specification labour and supervision & complete work as per drawings, specifications and instruction of Engineerqw-incharge. (Bolts, nuts, washers, U-clamps etc. for supporting shall be supplied by the Contractor within the rates quoted. These items will not be measured and paid seperately). The work is to be completed in all respect as per scope of work and specification. | Item251 | 300 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
252 | Notes: | Item252
253 | The quantities indicated are estimated values and hence are approximate. Final payment will be made based on actual quantities to be certified by the Purchaser. | Item253
254 | The cost of MS bolts (permanent and service(, washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants etc., as required for the work shall be deemed to be included in the quoted rates. | Item254
255 | All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accrodance with time schedule, are deemed be included in the quoted rates. | Item255
256 | CIVIL WORKS | Item256
257 | Site Grading Excavation in earth and filling to the grades and levels shown in the approved drawings in all kinds of conditions including for Road embarkments, using approved quality good earth from designated borrow area, for all heights and depths including clearing and stripping (min. 150mm) of the area marked for filling, taking spot levels, consolidating the exposed natural soil surface, excavating the earth from borrow area loading, transporting & unloading, spreading in layers not exceeding 150mm thickness, breaking clods, watering (if reqd.), ramming and compacting by manual/ mechanical means to give minimum 92% of modified Proctor's density of earth, testing & dressing including disposal of all unserviceable material all complete as per specifications and directions of Engineer-in-charge. | Item257 | 200 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
258 | (Rate to include cost of all labour, tools, tackles, equipment, hire charges, cost of borrow earth by way of royalties, right of way, cess etc., as applicable with all bye works and sundry works). | Item258
259 | Plain Cement Concrete Supplying and laying plain cement concrete (including shuttering of required) in all types of concrete works including levelling courses below foundation, substructure, superstrcuture, chambers, cable tranch, under floors and any other locations, at all leveies as per drawings, specifications and directions of the Engineer-in-charge. | Item259
260 | PCC 1:2:4 1 Cement : 2 Coarse sand : 4 stone aggregate 20mm nominal size. | Item260 | 500 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
261 | Reinforced Cement Concrete Providing and laying reinforced cement of grade M-20 with 20mm and down grade crushed stone aggregate in all types of structures like foundations, pedestals, pedestal bases, pipe supports, sleepers cable trench inlcuding constrcution joints, bitumen painting on surface in contact with soil, providing and fixing reinforcing steel, shuttering, inserts, finishes etc. at all depths and heights complete as per drawings, specifications and direction of the Engineer-incharge. | Item261 | 400 | M3 |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
262 | Rate to include cost of all labour, tools, tackles, equipment, hire charges, supply of all maerials such as minimum 43 grade cement including sulphate resistant cement for substructures, R/F steel, Inserts, bolts, conduits, bitumen, other minor constrcution materials, shuttering, stanging, earthwork in excavation and backfilling using serviceable earth in all conditions, shorting bailing and pumping out water, testing of concrete, curing etc. with all bye works and syndry works. | Item262
263 | TEMPORARY CATHODIC PROTECTION SYSTEM | Item263
264 | Design, detailed engineering, supply, installation, testing and commissioning of the temporary Cathodic protection system using Mg/ Zn galvanic anodes to protect the external surface of 3 LPE coated entire 5.5 km (approx.) long steel pipeline network against corrosion for design life of minimum 1 year or till commissioning of PCP system whichever is later as per standard specification No. MNGL/Steel/TS/15 for temporary cathodic protection system. Scope shall also include but not limited to the following for completion of jobs: | Item264
265 | Measurement of soil resistivity along the right of way of the main pipeline route as per specification for design & installation of anodes. | Item265
266 | Collection of additional data related to cathodic protection along the right of way of pipeline as per specifications. | Item266
267 | Supply, installation, testing & commissioning of one set of spark gap arrestor with 2 plate Zinc grounding cell of 20 kg net weight each across each insulating joint as per specification. | Item267
268 | Supply, installation, testing & commissioning one set of polarisation cell with zinc anode at all high tension (66KV or higher) electrical power transmission line/Equipment crossing or running parallel to the pipeline for grounding purpose as per specification. The rating shall depend upon anticipated fault current & ground bed resistance at the location of installation. However, the rating of polarisation cell (krick) shall not be less than 5 KA & number of 20 kg net weight zinc anode shall not be less than two. | Item268
269 | Supply & installation of Zinc Ribbon Anodes at 4-8 O’Clock position in the interval of 2 metre (max.) on carrier pipes at all cased crossings i.e. railways/ roads etc. | Item269
270 | Monitoring of the protection system for 6 months. | Item270
271 | All civil/ structural works related to TCP system including supply of bricks, cement & steel etc. required for completion of the system. | Item271
272 | For 12" | Item272 | 6000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
273 | For 6" | Item273 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
274 | For 4" | Item274 | 1500 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
275 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item275
276 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item276
277 | FIELD INSTRUMENTATION | Item277
278 | PRESSURE INSTRUMENTS | Item278
279 | Supply , Installation of Pressure Gagues and their accessories inclusive of supply of necessary piping materials and tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/ manifolds & hydraulic testing (exclusive of calibration of instruments) as per installation standard attached elsewhere in Tender Document and Supply as per Data Sheet No.MEC/23K8/05/E5/I/001/DS-PG. Give breakup of supply and Installation rate. | Item279 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
280 | CALIBRATION | Item280
281 | Calibration of the instruments listed below including removal of instruments from pre-installed locations like panels, enclosure racks, fields etc. and refixing them back in respective/ required places, providing equipments, necessary test jigs, instrument air and all consumables. Calibration reports shall be prepared and to be submitted to the Purchaser/ Consultant. | Item281
282 | Pressure Gauges | Item282 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
283 | Note: | Item283
284 | The quantities mentioned above are tentative and quantities for above including supply items shall be finalised & procured by Contractor only after due approval of EIC. Contractor supplied any surplus item during reconciliation shall not be accepted / taken by the Owner. | Item284
285 | For all the supply items mentioned above, procurement shall be made as per specification & Data Sheets, after due approval of Engineer-in-charge. | Item285
286 | Laying of MDPE pipe along with Steel pipe line Excluding supply of all MDPE pipe (PE 80/100,SDR11), but Including supply of Bends, Couplers, End caps, Tees, PE Reducer, CS to PE Fitting, Saddle Tapping, Warming mat, etc. as required to complete the job. ( Particular job specification.) "Receiving and taking-over" as defined in the specification, handling, loading, transportation and unloading of Owner supplied MDPE line pipes (PE80/100, SDR11) of all sizes (as free issue items) from Owner's designated place(s) of issue to Contractor's own stock-yard(s)/ Work Shop(s)/ work-site(s) including proper storing, stacking, identification, providing security & insurance cover , including supply of accessories of all sizes & thickness like Bends, Couplers, End caps, Tee, PE Reducer, CS to PE Fittings, Saddle Tapping, Warning Mat, etc.. | Item286
287 | Stringing/ uncoiling of the MDPE line pipe on the pipeline Right-of-Use, laying/ installation of MDPE line pipe alongwith steel pipeline (alongwith installation of required accessories as mentioned above) of following sizes, including executing all works; fabrication, access for construction; supply of all materials (except Owner supplied materials), consumables, labour and other incidental works and handing over the same after return of the surplus pipes to the Owner's designated stockyard(s); carrying out all temporary, ancillary, auxiliary works required to make the MDPE pipeline ready for commissioning as per drawings, specifications, scope of work indicated in PJS and other provisions of Contract document and instructions of Engineer-in-charge. | Item287
288 | UP to Dia 90mm | Item288 | 100 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
289 | Dia 125mm | Item289 | 2000 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
290 | Note : The quantities indicated above against all individual item are tentative and may vary considerably depending upon site condition, methodology adopted as per site requirement with due approval of Owner/ Consultants. | Item290
291 | PIPING WORKS FOR SECTIONALISING VALVE STATION-CUM-TAP-OFF POINT All works for fabriaction and installation of all piping above ground at all elevations and below ground at all depth for Sectionalising Valve Station alongwith preparation of construction drawings duly approved by EIC, in all type of terrains and soils including transportation and handling of all Owner supplied materials i.e. extended stem butt welded sectionalising gas actuated ball valve, other types of valves, line pipes for mainline, 4" NB pipe for all branch line including ventlines from Owner's designated place(s) of issue to work site. | Item291
292 | Contractor shall supply all required size & type of piping material like pipes, fittings & flanges etc. as per PMS alongwith 2" NB pipe for all branch line & vent line (wherever required) including supply of all consumables, manpower, machinaries, materials etc. and carrying out all mechanical works of underground and above ground piping including fabrication, welding, nondestructive testing of welds, weld repairs/ retesting, cleaning/ flushing, pre-hydrotesting & hydrostatic testing, dewatering, functional testing, cutting of mainline and bevelling (if required) | Item292
293 | assembly, including radiography of tie-in joints, corrosion, coating and external painting as required, installation of instruments like pressure/ temperature instruments/ gauges alongwith complete SS Tubing works including supply of SS Tube and thier accessories etc., as required, obtaining all statutory clearances, approvals and permissions for the works (wherever required), making of valve pit (for detail refer relevant drawings) for SV Stationscum- tap-off points enclosed with tender filled with sand, excavation and filling in all types of soils including soft/ hard rock for installation of piping/ pipe supports providing pipe supports, area fencing and gate including all associated civil and structural works; painting, finishing, clean-up and restoration of site; preparation of as-built drawings, documents and project records and performing all works as per drawings, specifications, other provisions of Contract document and instructions of Engineer-in-charge. In this item, instead of Brick Work RCC will be done | Item293
294 | Type - I SV Station on 12" Pipeline | Item294 | 1 | Lumpsum for each |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
295 | Note: i) Work under above items are exclusive of all works associated with main pipeline covered under Item No. 1.0 above. ii) All civil/ structural works including area fencing and gate, valve pits except for piping support will be paid separately as per unit rate provided elsewhere in the SOR. iii) All coupling, nipples etc. as required shall be suplied by contractor but no separate payments shall be made as it is covered under above item rate. | Item295
296 | Details of Major Road Crossing (Canal/SH/DR/NHAI): Supply, Installation & Insertion of pipeline across Canal / State Highways as per SCC and technical specifications | Item296
297 | Supply & Installation of 24" NB x 6.4mm Wall thk. Casing pipe for Line Pipe 12"NB(6.4 mm thk API 5L Gr X52) & 4" NB, 6.4 mm thk API 5L Gr. X52 pipe by Jacking Boring . Including Insertion of 12" dia and 4" dia (for 125 mm dia MDPE Connectivity) Carrier pipeline in 24" dia casing pipe and connectivity with existing pipeline at both end of National Highways/State Highways/ Railway as per SCC and technical specifications -Supply of Casing Pipe Supply of following casing pipe including handling, loading, transportation & unloading etc. to contractor's own stock yard / worksite(s). -After Completion of insertion of carrier pipe with Connectivity at both end including all works as per the scope of work -Post Hydro testing & Commissioning , Submission of as-built drawing, Submission of Documents - The rates shall include bore holes for soil investigation, collection of disturbed samples from bore holes and visual engineering classification of soil at crossing location. Minimum 2 nos of bore holes ( 01 no each at both end of crossing) are required on each crossing and submission of detailed report to Company.Boreholes shall be made at locations as direct by Engineer in-charge at crossing location to find out the presence of rock strata. Boring shall be carried out in accordance with the provision of IS:1892. Minimum diameter of boring shall be 150 mm. - Rate Should include supply & installation of 250mm Casing pipe for 4" Steel Pipeline for MDPE (if required by Authority & as per the instructions of EIC) | Item297
298 | Note: (i) Crossing width may vary as per site condition. Tenderer are advised to visit site for actual assessment of extent of crossing. Actual length of Boring shall be as per design calculations so that pipe is not under stress as permitted by codes/ specifications. However final length of string & cover from top of pipe shall be decided by concerned Authority/ Engineer-in-charge. (ii) Payment for the length of final tied-in carrier pipeline string with mainline made for crossing laid by Boring method are inclusive in the above item rate and no separate payment shall be made under other item mentioned elsewhere. | Item298
299 | (iii) The Contractor has to quote alongwith 4" NB (for 125mm MDPE). No any extra payment shall be made against this item. (iv) Width of above crossings indicated are tentative. The width indicated are not for any single crossings. This shall be as per requirement at site for crossings at different locations. | Item299
300 | (v) Actual length & cover from top of casing pipe string may vary depending upon site conditions, approved drawings, specification etc. and / or as decided by concerned Authority / Engineer-in-charge. (vi) No Extra Payment for supply & installation of Zinc ribbon to be provided to Carrier pipe & Zinc Anode is to be provided to Casing pipe and its design included in above item | Item300
301 | Supply and installation of 24'' casing pipe,Preparation of required length of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and specification/ drawings. Insertion of carrier pipeline welded string including all other works as mentioned in item no. 1.0 above and as per specification/ drawings. Insertion of carrier pipe in casing pipe after above ground pretesting at specified test pressure and installation of casing insulators & Zinc ribbon anode as per specification/ drawings. Installation of vent and drain assembly, fixing of end seals, backfilling and restoration as original of the facilities crossed and performing all other works including pigging, cleaning, final hydrotesting etc. alongwith mainline works (as mentioned in item no. 1.0 above) and as per specification, approved procedure, drawing etc. and instruction of Engineer-in-charge and provision of contract document, getting NOC from all concerned Authority of the facilities crossed (Any type of soil) | Item301 | 140 | Mtrs |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | 0 | [36 empty] | 0 | 0 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
Total in Figures | [51 empty] | 0 | 0 | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information